{"text_format":"1","workbook":"xlsx","n_sheets":7,"sheets":["Instructions","Instructional Infographic","Fillable Worksheet","Worksheet (Example)","ASHRAE Design Levels","Glossary of Terms","Worksheet with Additional Info"],"not_rendered":{"charts":0,"images":6,"macros":1,"external_links":1,"defined_names":15,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Instructions","index":0,"n_rows":23,"n_cols":1,"rows_kept":23,"cut":false,"hidden":false,"merged":[[14,0,14,8],[22,0,22,8],[11,0,11,7],[12,0,12,8],[17,0,17,8],[18,0,18,8],[19,0,19,8],[21,0,21,8],[20,0,20,8],[15,0,15,8],[0,0,0,8],[1,0,1,8],[5,0,5,8],[6,0,6,8],[10,0,10,8],[2,0,2,8],[4,0,4,8],[7,0,7,8],[8,0,8,7],[9,0,9,8]]}
[" Instructions"]
["This Air Change Rate Calculator is a tool for calculating air flow rates for lab space based on the ventilation risk present. The fillable worksheet contains the basic information necessary to calculate air change rates and can be copied and adjusted to suit your lab's needs. (Additional fields for users seeking further detail is provided in the \"Worksheet with Additional Info\" Tab.)"]
["Before completing this worksheet, a survey of the lab space should be conducted be a qualified professional to determine system information and a risk level number (or RCB) for each lab space (Refer to the Laboratory Ventilation Risk Assessment Tool (LVRA Tool) and LVRA User Guide). Once  the risk level for each lab space is determined using the LVRA Tool, follow these instructions, supplemented by the Instructional Infographic. "]
[]
["1. Enter Room Information"]
["In each row, enter information for each room/labspace, including its number, name, area, and height. It is recommended that you create a separate tab for each floor of the lab building being evaluated. "]
["Select the risk level (also refered to as risk control band) number from the dropdown for each room. This worksheet automatically color codes risk control bands as a visual que for surveyors. Upon choosing the risk level, recommended air changes (occupied and unoccupied) will be provided in the following columns based on following ASHRAE Design Levels and ASHRAE 62.1 guidelines.  See the ASHRAE Design Levels tab and  Glossary of Terms: Risk Control Band for more info."]
[]
["2. Enter Available Supply System Information"]
[" Enter information for the laboratory supply system gathered during the Lab Space Survey"]
[]
["3. Enter Exhaust System Information"]
[" Enter information for exposure control devices and exhaust  gathered during the Exposure Control Device survey. "]
[]
["4. Enter Exhaust and Exposure Control Device Information"]
["The exhaust type, size, and quantity will determine the room flow rates. Enter all available information for each exhaust device in the lab space. Detailed information is necessary to provide accurate calculations, especially regarding fume hoods. "]
[]
["4. Resultant Air Change Rate"]
["Resultant Air Changes per Hour (ACH) will be calculated automatically by formulas integrated into the spreadsheet. See the Instructional Infographic for detailed descriptions of formulas used in this calculator.\n"]
["A Note on Additions"]
["To add additional rooms, copy whole row for a room and paste below last row. Double check all calculations are as expected using the formulas provided on the instructional infographic. "]
["If adding additional lines (e.g. additional valves or box numbers), insert a row in the middle of the merged cells and double check that calculations are as expected. "]
["Disclaimer: This tool is designed to serve as a guide and can be modified to suit your institution's needs.                                        All calculations should be thoroughly reviewed by laboratory ventilation specialists prior to commissioning to ensure proper ventilation system design."]

{"sheet":"Instructional Infographic","index":1,"n_rows":21,"n_cols":46,"rows_kept":21,"cut":false,"hidden":false,"merged":[[11,0,21,0],[3,37,3,38],[13,23,13,27],[2,41,2,44],[3,41,3,44],[2,17,2,40],[3,39,3,40],[2,1,2,7],[3,10,3,14],[3,15,3,16],[3,17,3,22],[3,32,3,34],[3,35,3,36],[2,10,2,16],[5,5,10,5],[5,6,10,6],[5,7,10,7],[5,0,10,0],[5,1,10,1],[5,2,10,2],[5,3,10,3],[5,4,10,4],[5,43,10,43],[5,44,10,44],[13,7,13,14],[14,10,14,14],[5,38,10,38],[5,39,10,39],[5,40,10,40],[5,41,10,41],[5,42,10,42],[5,35,10,35],[5,36,10,36],[5,37,10,37],[5,8,10,8],[21,7,21,14],[3,23,3,29],[13,31,13,32],[15,10,15,14],[16,10,16,14],[17,10,17,14],[18,10,18,14],[19,10,19,14],[20,7,20,14],[5,9,10,9],[5,10,10,10],[5,15,10,15],[5,16,10,16],[5,17,10,17],[20,31,20,32]]}
[]
[]
[null,"Room Information",null,null,null,null,null,null,null,null,"Supply",null,null,null,null,null,null,"Exhaust",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Results"]
[null,null,null,null,null,null,null,null,null,null,"System Info",null,null,null,null,"Room Supply Flows",null,"System Info",null,null,null,null,null,"Fume Hood Info",null,null,null,null,null,null,null,null,"Box Flows",null,null,"Room Flow, Qex, (based on Exhaust Devices)",null,"Room Flow, Qex, (based on ACH)",null,"Room Exhaust Flows",null,"Air Change Rates"]
[null,"Room #","Room Name","Area\n(ft2)","Height\n(ft)","Volume\n(ft3)","Room Type","Risk Level #","ASHRAE Recommended Room Air Changes  (Occupied) ","ASHRAE Recommended Room Air Changes (Unoccupied) ","AHU #","VAV Box #","Box Size","Box Max Flows (cfm)","Box Min Flows (cfm)","Room Flow @ Min\n(cfm)","Room Flow @ Max\n(cfm)","Exh. Fan #","VVE Box #","Box        Size","Max Box Flows (cfm)","Min Box Flows (cfm)","Exhaust\nType","Total Width (Ft)","Device Height (in)","Face Width (in)","Hood Depth* (in)","Opening Height (in)","Hood Interior Volume (ft3)","Face Area (ft2)","Face velocity (FPM)","RCB Rating ","Min ACH based on RCB rating ","Min Flow (Based on RCB rating & size)\n(cfm)","Max Flow (FH @ 18 in.)\n(cfm)","Room Min Flow\n(ECDs @ Min)\n(cfm)","Room Max Flow\n(ECDs @ Max)\n(cfm)","Room Min Flow\n(cfm)","Room Max Flow\n(cfm)","Room Min Flow\n(cfm)","Room Min Flow\n(cfm)","Min ACH","Max ACH","Min\ncfm/sf","Max\ncfm/sf","Notes"]
["Example","3111","Tissue Culture",324,9,{"$f":"D6*E6","v":2916},"Lab",2,{"$f":"VLOOKUP(H6,$H$16:$I$20,2,TRUE)","v":4},{"$f":"VLOOKUP(H6,$H$16:$J$20,3,TRUE)","v":1.7},"AH-1,   AH-3","M49",110,null,50,{"$f":"AN6*0.9","v":263.54166666666669},{"$f":"AO6*0.9","v":1687.5},"EAH-1, EAH-3","M71",110,{"$f":"AI6","v":475},{"$f":"AH6","v":60.69444444444445},"FH",4,48,{"$f":"X6*12-10","v":38},23,18,{"$f":"AA6*Z6*Y6/(12*12*12)","v":24.277777777777779},{"$f":"AB6*Z6/(12*12)","v":4.75},100,1,{"$f":"VLOOKUP(AF6,$AF$16:$AG$20,2,TRUE)","v":150},{"$f":"AG6*AC6/60","v":60.69444444444445},{"$f":"AE6*AD6","v":475},{"$f":"SUM(AH6:AH11)","v":292.82407407407408},{"$f":"SUM(AI6:AI11)","v":1875},{"$f":"J6*F6/60","v":82.61999999999999},{"$f":"I6*F6/60","v":194.4},{"$f":"MAX(AJ6,AM6)","v":292.82407407407408},{"$f":"MAX(AK6,AM6)","v":1875},{"$f":"AN6*60/F6","v":6.025186709343088},{"$f":"AO6*60/F6","v":38.580246913580247},{"$f":"AN6/D6","v":0.90377800640146322},{"$f":"AO6/D6","v":5.7870370370370372}]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,null,null,null,null,"M72",110,{"$f":"AI7","v":625},{"$f":"AH7","v":133.10185185185185},"FH",5,48,{"$f":"X7*12-10","v":50},23,18,{"$f":"AA7*Z7*Y7/(12*12*12)","v":31.944444444444443},{"$f":"AB7*Z7/(12*12)","v":6.25},100,3,{"$f":"VLOOKUP(AF7,$AF$16:$AG$20,2,TRUE)","v":250},{"$f":"AG7*AC7/60","v":133.10185185185185},{"$f":"AE7*AD7","v":625}]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,null,null,null,null,"M73",null,775,{"$f":"AH8","v":99.027777777777786},"FH",6,48,{"$f":"X8*12-10","v":62},23,18,{"$f":"AA8*Z8*Y8/(12*12*12)","v":39.611111111111114},{"$f":"AB8*Z8/(12*12)","v":7.75},100,1,{"$f":"VLOOKUP(AF8,$AF$16:$AG$20,2,TRUE)","v":150},{"$f":"AG8*AC8/60","v":99.027777777777786},{"$f":"AE8*AD8","v":775}]
[]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,null,null,null,null,"-",null,null,"","BSC"]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,null,null,null,null,"M5",110,null,null,"GX",null,null,null,null,null,null,null,null,null,null,0,0]
["Formulas Explained"]
[]
[null,null,null,null,null,null,null,"Room Air Change Recommendations based on Risk Levelᶧ ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Typical Dimensions",null,null,null,null,null,null,null,"Fumehood"]
[null,null,null,null,null,null,null,"Risk Level","Air changes (Occupied)","Air changes (Unoccupied)","Notes ",null,null,null,null,null,null,null,null,null,null,null,null,"Fume Hood Width","Fume Hood Height","Fume Face Width","Fume Hood Depth","Fume Hood Opening Height",null,null,null,"Risk Level","Minimum Air changes inside fumehoodᶧᶧ "]
[null,null,null,null,null,null,null,0,1.7,1.7,"Based on ASHRAE 62.1",null,null,null,null,null,null,null,null,null,null,null,null,"4'","48\"","Varies ","23\" to 27\"","18\"",null,null,null,0,150]
[null,null,null,null,null,null,null,1,1.7,1.7,"Based on ASHRAE 62.1",null,null,null,null,null,null,null,null,null,null,null,null,"5'","48\"",null,null,"18\"",null,null,null,1,150]
[null,null,null,null,null,null,null,2,4,1.7,"4 to 6 recommended",null,null,null,null,null,null,null,null,null,null,null,null,"6'","48\"",null,null,"18\"",null,null,null,2,150]
[null,null,null,null,null,null,null,3,6,4,"6 to 8 recommended",null,null,null,null,null,null,null,null,null,null,null,null,"8'","48\"",null,null,"18\"",null,null,null,3,250]
[null,null,null,null,null,null,null,4,8,4,"8 or more",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,375]
[null,null,null,null,null,null,null,"ᶧRecommendations are from ASHRAE Classification of Laboratory Ventilation Design Levels",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"ᶧᶧ From ANSI Standard Z9.5"]

{"sheet":"Fillable Worksheet","index":2,"n_rows":57,"n_cols":46,"rows_kept":57,"cut":false,"hidden":false,"merged":[[40,41,45,41],[40,42,45,42],[40,43,45,43],[40,44,45,44],[40,16,45,16],[40,17,45,17],[40,35,45,35],[40,36,45,36],[40,37,45,37],[40,38,45,38],[40,15,45,15],[40,0,45,0],[40,1,45,1],[40,2,45,2],[40,3,45,3],[40,4,45,4],[40,5,45,5],[40,39,45,39],[40,40,45,40],[33,41,38,41],[33,42,38,42],[33,43,38,43],[33,44,38,44],[33,16,38,16],[33,17,38,17],[33,35,38,35],[33,36,38,36],[33,37,38,37],[33,38,38,38],[33,15,38,15],[33,0,38,0],[33,1,38,1],[33,2,38,2],[33,3,38,3],[33,4,38,4],[33,5,38,5],[33,39,38,39],[33,40,38,40],[26,0,31,0],[26,1,31,1],[26,2,31,2],[26,3,31,3],[26,4,31,4],[26,5,31,5],[26,39,31,39],[26,40,31,40],[26,41,31,41],[26,16,31,16],[26,17,31,17],[26,35,31,35],[26,36,31,36],[26,37,31,37],[26,38,31,38],[19,44,24,44],[19,16,24,16],[19,17,24,17],[19,35,24,35],[19,36,24,36],[19,37,24,37],[19,38,24,38],[26,6,31,6],[26,7,31,7],[26,8,31,8],[26,9,31,9],[26,10,31,10],[26,15,31,15],[26,42,31,42],[26,43,31,43],[26,44,31,44],[19,15,24,15],[12,41,17,41],[12,42,17,42],[12,43,17,43],[19,39,24,39],[19,40,24,40],[19,41,24,41],[19,42,24,42],[19,43,24,43],[54,10,54,14],[55,10,55,14],[56,7,56,14],[12,44,17,44],[19,0,24,0],[19,1,24,1],[19,2,24,2],[19,3,24,3],[19,4,24,4],[19,5,24,5],[12,35,17,35],[12,36,17,36],[12,37,17,37],[12,38,17,38],[12,39,17,39],[12,40,17,40],[12,8,17,8],[12,9,17,9],[12,10,17,10],[12,15,17,15],[12,16,17,16],[12,17,17,17],[19,6,24,6],[19,7,24,7],[12,2,17,2],[12,3,17,3],[12,4,17,4],[12,5,17,5],[12,6,17,6],[12,7,17,7],[51,10,51,14],[52,10,52,14],[53,10,53,14],[19,8,24,8],[19,9,24,9],[19,10,24,10],[33,6,38,6],[33,7,38,7],[33,8,38,8],[33,9,38,9],[33,10,38,10],[40,6,45,6],[40,7,45,7],[40,8,45,8],[40,9,45,9],[40,10,45,10],[5,42,10,42],[5,43,10,43],[5,44,10,44],[47,0,57,0],[49,7,49,14],[49,23,49,27],[49,31,49,32],[50,10,50,14],[5,17,10,17],[5,35,10,35],[5,36,10,36],[5,37,10,37],[5,38,10,38],[5,39,10,39],[5,7,10,7],[5,8,10,8],[5,9,10,9],[5,10,10,10],[5,15,10,15],[5,16,10,16],[56,31,56,32],[57,7,57,14],[12,0,17,0],[12,1,17,1],[5,0,10,0],[5,1,10,1],[5,2,10,2],[5,3,10,3],[5,4,10,4],[5,5,10,5],[5,6,10,6],[5,40,10,40],[5,41,10,41],[2,1,2,7],[2,10,2,16],[2,17,2,40],[2,41,2,44],[3,10,3,14],[3,15,3,16],[3,17,3,22],[3,23,3,29],[3,32,3,34],[3,35,3,36],[3,37,3,38],[3,39,3,40],[3,41,3,44]]}
[]
[]
[null,"Room Information",null,null,null,null,null,null,null,null,"Supply",null,null,null,null,null,null,"Exhaust",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Results"]
[null,null,null,null,null,null,null,null,null,null,"System Info",null,null,null,null,"Room Supply Flows",null,"System Info",null,null,null,null,null,"Fume Hood Info",null,null,null,null,null,null,null,null,"Box Flows",null,null,"Room Flow, Qex, (based on Exhaust Devices)",null,"Room Flow, Qex, (based on ACH)",null,"Room Exhaust Flows",null,"Air Change Rates"]
[null,"Room #","Room Name","Area\n(ft2)","Height\n(ft)","Volume\n(ft3)","Room Type","Risk Level #","ASHRAE Recommended Room Air Changes  (Occupied) ","ASHRAE Recommended Room Air Changes (Unoccupied) ","AHU #","VAV Box #","Box Size","Box Max Flows (cfm)","Box Min Flows (cfm)","Room Flow @ Max\n(cfm)","Room Flow @ Min\n(cfm)","Exh. Fan #","VVE Box #","Box        Size","Max Box Flows (cfm)","Min Box Flows (cfm)","Exhaust\nType","Total Width (Ft)","Device Height (in)","Face Width (in)","Hood Depth* (in)","Opening Height (in)","Hood Interior Volume (ft3)","Face Area (ft2)","Face velocity (FPM)","RCB Rating ","Min ACH based on RCB rating ","Min Flow (Based on RCB rating & size)\n(cfm)","Max Flow (FH @ 18 in.)\n(cfm)","Room Min Flow\n(ECDs @ Min)\n(cfm)","Room Max Flow\n(ECDs @ Max)\n(cfm)","Room Min Flow\n(cfm)","Room Max Flow\n(cfm)","Room Min Flow\n(cfm)","Room Min Flow\n(cfm)","Max ACH","Min ACH","Max\ncfm/sf","Min\ncfm/sf","Notes"]
["Example","3111","Tissue Culture",324,9,{"$f":"D6*E6","v":2916},"Lab",2,{"$f":"VLOOKUP(H6,$H$52:$I$56,2,TRUE)","v":4},{"$f":"VLOOKUP(H6,$H$52:$J$56,3,TRUE)","v":1.7},"AH-1,   AH-3","M49",110,null,50,{"$f":"AN6*0.9","v":263.54166666666669},{"$f":"AO6*0.9","v":1687.5},"EAH-1, EAH-3","M71",110,null,{"$f":"AH6","v":60.69444444444445},"FH",4,48,{"$f":"X6*12-10","v":38},23,18,{"$f":"AA6*Z6*Y6/(12*12*12)","v":24.277777777777779},{"$f":"AB6*Z6/(12*12)","v":4.75},100,1,{"$f":"VLOOKUP(AF6,$AF$52:$AG$56,2,TRUE)","v":150},{"$f":"AG6*AC6/60","v":60.69444444444445},{"$f":"AE6*AD6","v":475},{"$f":"SUM(AH6:AH11)","v":292.82407407407408},{"$f":"SUM(AI6:AI11)","v":1875},{"$f":"J6*F6/60","v":82.61999999999999},{"$f":"I6*F6/60","v":194.4},{"$f":"MAX(AJ6,AM6)","v":292.82407407407408},{"$f":"MAX(AK6,AM6)","v":1875},{"$f":"AN6*60/F6","v":6.025186709343088},{"$f":"AO6*60/F6","v":38.580246913580247},{"$f":"AN6/D6","v":0.90377800640146322},{"$f":"AO6/D6","v":5.7870370370370372}]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,null,null,null,null,"M72",110,null,50,"FH",5,48,{"$f":"X7*12-10","v":50},23,18,{"$f":"AA7*Z7*Y7/(12*12*12)","v":31.944444444444443},{"$f":"AB7*Z7/(12*12)","v":6.25},100,3,{"$f":"VLOOKUP(AF7,$AF$52:$AG$56,2,TRUE)","v":250},{"$f":"AG7*AC7/60","v":133.10185185185185},{"$f":"AE7*AD7","v":625}]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,null,null,null,null,"-",null,null,"","FH",6,48,{"$f":"X8*12-10","v":62},23,18,{"$f":"AA8*Z8*Y8/(12*12*12)","v":39.611111111111114},{"$f":"AB8*Z8/(12*12)","v":7.75},100,1,{"$f":"VLOOKUP(AF8,$AF$52:$AG$56,2,TRUE)","v":150},{"$f":"AG8*AC8/60","v":99.027777777777786},{"$f":"AE8*AD8","v":775}]
[]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,null,null,null,null,"-",null,null,"","BSC"]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,null,null,null,null,"M5",110,null,50,"GX",null,null,null,null,null,null,null,null,null,null,0,0]
[]
[null,null,null,null,null,{"$f":"D13*E13","v":0},"Lab",null,{"$f":"VLOOKUP(H13,$H$52:$I$56,2,TRUE)","v":1.7},{"$f":"VLOOKUP(H13,$H$52:$J$56,3,TRUE)","v":1.7},null,null,null,null,null,{"$f":"AN13*0.9","v":0},{"$f":"AO13*0.9","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(AF13,$AF$52:$AG$56,2,TRUE)","v":150},{"$f":"AG13*AC13/60","v":0},{"$f":"AE13*AD13","v":0},{"$f":"SUM(AH13:AH18)","v":0},0,{"$f":"J13*F13/60","v":0},{"$f":"I13*F13/60","v":0},{"$f":"MAX(AJ13,AM13)","v":0},{"$f":"MAX(AK13,AM13)","v":0},{"$f":"AN13*60/F13","v":{"$error":"#DIV/0!"}},{"$f":"AO13*60/F13","v":{"$error":"#DIV/0!"}},{"$f":"AN13/D13","v":{"$error":"#DIV/0!"}},{"$f":"AO13/D13","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(AF14,$AF$52:$AG$56,2,TRUE)","v":150},0,0]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,150,0,0]
[]
[null,null,null,null,null,0]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[]
[null,null,null,null,null,{"$f":"D20*E20","v":0},"Lab",null,{"$f":"VLOOKUP(H20,$H$52:$I$56,2,TRUE)","v":1.7},{"$f":"VLOOKUP(H20,$H$52:$J$56,3,TRUE)","v":1.7},null,null,null,null,null,{"$f":"AN20*0.9","v":0},{"$f":"AO20*0.9","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(AF20,$AF$52:$AG$56,2,TRUE)","v":150},{"$f":"AG20*AC20/60","v":0},{"$f":"AE20*AD20","v":0},{"$f":"SUM(AH20:AH25)","v":0},0,{"$f":"J20*F20/60","v":0},{"$f":"I20*F20/60","v":0},{"$f":"MAX(AJ20,AM20)","v":0},{"$f":"MAX(AK20,AM20)","v":0},{"$f":"AN20*60/F20","v":{"$error":"#DIV/0!"}},{"$f":"AO20*60/F20","v":{"$error":"#DIV/0!"}},{"$f":"AN20/D20","v":{"$error":"#DIV/0!"}},{"$f":"AO20/D20","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,150,0,0]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,150,0,0]
[]
[null,null,null,null,null,0]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[]
[null,null,null,null,null,{"$f":"D27*E27","v":0},"Lab",null,{"$f":"VLOOKUP(H27,$H$52:$I$56,2,TRUE)","v":1.7},{"$f":"VLOOKUP(H27,$H$52:$J$56,3,TRUE)","v":1.7},null,null,null,null,null,{"$f":"AN27*0.9","v":0},{"$f":"AO27*0.9","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(AF27,$AF$52:$AG$56,2,TRUE)","v":150},{"$f":"AG27*AC27/60","v":0},{"$f":"AE27*AD27","v":0},{"$f":"SUM(AH27:AH32)","v":0},0,{"$f":"J27*F27/60","v":0},{"$f":"I27*F27/60","v":0},{"$f":"MAX(AJ27,AM27)","v":0},{"$f":"MAX(AK27,AM27)","v":0},{"$f":"AN27*60/F27","v":{"$error":"#DIV/0!"}},{"$f":"AO27*60/F27","v":{"$error":"#DIV/0!"}},{"$f":"AN27/D27","v":{"$error":"#DIV/0!"}},{"$f":"AO27/D27","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,150,0,0]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,150,0,0]
[]
[null,null,null,null,null,0]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[]
[null,null,null,null,null,{"$f":"D34*E34","v":0},"Lab",null,{"$f":"VLOOKUP(H34,$H$52:$I$56,2,TRUE)","v":1.7},{"$f":"VLOOKUP(H34,$H$52:$J$56,3,TRUE)","v":1.7},null,null,null,null,null,{"$f":"AN34*0.9","v":0},{"$f":"AO34*0.9","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(AF34,$AF$52:$AG$56,2,TRUE)","v":150},{"$f":"AG34*AC34/60","v":0},{"$f":"AE34*AD34","v":0},{"$f":"SUM(AH34:AH39)","v":0},0,{"$f":"J34*F34/60","v":0},{"$f":"I34*F34/60","v":0},{"$f":"MAX(AJ34,AM34)","v":0},{"$f":"MAX(AK34,AM34)","v":0},{"$f":"AN34*60/F34","v":{"$error":"#DIV/0!"}},{"$f":"AO34*60/F34","v":{"$error":"#DIV/0!"}},{"$f":"AN34/D34","v":{"$error":"#DIV/0!"}},{"$f":"AO34/D34","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,150,0,0]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,150,0,0]
[]
[null,null,null,null,null,0]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[]
[null,null,null,null,null,{"$f":"D41*E41","v":0},"Lab",null,{"$f":"VLOOKUP(H41,$H$52:$I$56,2,TRUE)","v":1.7},{"$f":"VLOOKUP(H41,$H$52:$J$56,3,TRUE)","v":1.7},null,null,null,null,null,{"$f":"AN41*0.9","v":0},{"$f":"AO41*0.9","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP(AF41,$AF$52:$AG$56,2,TRUE)","v":150},{"$f":"AG41*AC41/60","v":0},{"$f":"AE41*AD41","v":0},{"$f":"SUM(AH41:AH46)","v":0},0,{"$f":"J41*F41/60","v":0},{"$f":"I41*F41/60","v":0},{"$f":"MAX(AJ41,AM41)","v":0},{"$f":"MAX(AK41,AM41)","v":0},{"$f":"AN41*60/F41","v":{"$error":"#DIV/0!"}},{"$f":"AO41*60/F41","v":{"$error":"#DIV/0!"}},{"$f":"AN41/D41","v":{"$error":"#DIV/0!"}},{"$f":"AO41/D41","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,150,0,0]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,150,0,0]
[]
[null,null,null,null,null,0]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[]
["Do Not Delete"]
[]
[null,null,null,null,null,null,null,"Room Air Change Recommendations based on Risk Levelᶧ ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Typical Dimensions",null,null,null,null,null,null,null,"Fumehood"]
[null,null,null,null,null,null,null,"Risk Level","Air changes (Occupied)","Air changes (Unoccupied)","Notes ",null,null,null,null,null,null,null,null,null,null,null,null,"Fume Hood Width","Fume Hood Height","Fume Face Width","Fume Hood Depth","Fume Hood Opening Height",null,null,null,"Risk Level","Minimum Air changes inside fumehoodᶧᶧ "]
[null,null,null,null,null,null,null,0,1.7,1.7,"Based on ASHRAE 62.1",null,null,null,null,null,null,null,null,null,null,null,null,4,"48\"","Varies ","23\"","18\"",null,null,null,0,150]
[null,null,null,null,null,null,null,1,1.7,1.7,"Based on ASHRAE 62.1",null,null,null,null,null,null,null,null,null,null,null,null,5,null,null,"27\"",null,null,null,null,1,150]
[null,null,null,null,null,null,null,2,4,1.7,"4 to 6 recommended",null,null,null,null,null,null,null,null,null,null,null,null,6,null,null,null,null,null,null,null,2,150]
[null,null,null,null,null,null,null,3,6,4,"6 to 8 recommended",null,null,null,null,null,null,null,null,null,null,null,null,8,null,null,null,null,null,null,null,3,250]
[null,null,null,null,null,null,null,4,8,4,"8 or more",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,250]
[null,null,null,null,null,null,null,"ᶧRecommendations are from ASHRAE Classification of Laboratory Ventilation Design Levels",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"ᶧᶧ From ANSI Standard Z9.5"]

{"sheet":"Worksheet (Example)","index":3,"n_rows":119,"n_cols":81,"rows_kept":119,"cut":false,"hidden":false,"merged":[[6,0,11,0],[6,1,11,1],[6,2,11,2],[6,3,11,3],[6,4,11,4],[6,5,11,5],[6,6,11,6],[6,7,11,7],[6,8,11,8],[6,10,11,10],[6,14,11,14],[6,15,11,15],[6,16,11,16],[6,17,11,17],[6,18,11,18],[6,19,11,19],[6,20,11,20],[6,62,11,62],[6,63,11,63],[6,64,11,64],[6,65,11,65],[6,75,11,75],[6,76,11,76],[6,77,11,77],[6,78,11,78],[3,66,3,67],[6,21,11,21],[6,31,11,31],[6,32,11,32],[6,33,11,33],[6,35,11,35],[6,56,11,56],[6,57,11,57],[6,58,11,58],[6,59,11,59],[6,60,11,60],[1,35,1,69],[1,75,1,78],[2,10,2,13],[2,14,2,15],[2,16,2,17],[2,18,2,19],[2,20,2,21],[2,22,2,25],[2,26,2,27],[2,28,2,29],[2,35,2,39],[2,40,2,48],[2,49,2,51],[2,52,2,55],[2,56,2,57],[2,58,2,59],[2,60,2,61],[2,62,2,63],[2,64,2,65],[115,17,117,17],[115,18,117,18],[115,19,117,19],[115,20,117,20],[115,21,117,21],[115,31,117,31],[115,7,117,7],[2,80,3,80],[3,10,3,13],[3,16,3,17],[3,18,3,19],[3,20,3,21],[3,22,3,23],[3,24,3,25],[3,26,3,27],[3,28,3,29],[3,35,3,39],[3,40,3,48],[3,56,3,57],[3,58,3,59],[2,66,2,69],[2,70,2,71],[2,75,2,77],[3,60,3,61],[3,64,3,65],[3,68,3,69],[3,70,3,71],[3,75,3,78],[6,61,11,61],[1,1,3,8],[1,10,1,29],[1,31,2,33],[115,65,117,65],[115,75,117,75],[115,76,117,76],[115,77,117,77],[115,78,117,78],[116,39,117,39],[116,50,117,50],[116,51,117,51],[115,59,117,59],[115,60,117,60],[115,61,117,61],[115,62,117,62],[115,63,117,63],[115,64,117,64],[115,32,117,32],[115,33,117,33],[115,35,117,35],[115,56,117,56],[115,57,117,57],[115,58,117,58],[115,8,117,8],[115,10,117,10],[115,14,117,14],[115,15,117,15],[115,16,117,16],[115,1,117,1],[115,2,117,2],[115,3,117,3],[115,4,117,4],[115,5,117,5],[115,6,117,6],[111,15,113,15],[108,65,109,65],[108,75,109,75],[108,76,109,76],[108,77,109,77],[108,78,109,78],[111,64,113,64],[111,65,113,65],[111,75,113,75],[111,76,113,76],[111,77,113,77],[111,78,113,78],[111,58,113,58],[111,59,113,59],[111,60,113,60],[111,61,113,61],[111,62,113,62],[111,63,113,63],[111,31,113,31],[111,32,113,32],[111,33,113,33],[108,7,109,7],[108,8,109,8],[108,10,109,10],[108,14,109,14],[108,15,109,15],[108,16,109,16],[111,35,113,35],[111,56,113,56],[111,57,113,57],[111,16,113,16],[111,17,113,17],[111,18,113,18],[111,19,113,19],[111,20,113,20],[111,21,113,21],[111,1,113,1],[111,2,113,2],[111,3,113,3],[111,4,113,4],[111,5,113,5],[108,1,109,1],[108,2,109,2],[108,3,109,3],[108,4,109,4],[108,5,109,5],[108,6,109,6],[111,6,113,6],[111,7,113,7],[111,8,113,8],[111,10,113,10],[111,14,113,14],[104,35,106,35],[104,56,106,56],[104,57,106,57],[105,39,106,39],[105,50,106,50],[105,51,106,51],[108,62,109,62],[108,63,109,63],[108,64,109,64],[108,32,109,32],[108,33,109,33],[108,35,109,35],[108,56,109,56],[108,57,109,57],[108,58,109,58],[108,17,109,17],[108,18,109,18],[108,19,109,19],[108,20,109,20],[108,21,109,21],[108,31,109,31],[108,59,109,59],[108,60,109,60],[108,61,109,61],[104,16,106,16],[104,17,106,17],[104,18,106,18],[104,19,106,19],[104,20,106,20],[104,21,106,21],[104,6,106,6],[104,7,106,7],[104,8,106,8],[104,10,106,10],[104,14,106,14],[104,15,106,15],[101,65,102,65],[101,75,102,75],[101,76,102,76],[101,77,102,77],[101,78,102,78],[104,64,106,64],[104,65,106,65],[104,75,106,75],[104,76,106,76],[104,77,106,77],[104,78,106,78],[104,58,106,58],[104,59,106,59],[104,60,106,60],[104,61,106,61],[104,62,106,62],[104,63,106,63],[104,31,106,31],[104,32,106,32],[104,33,106,33],[104,1,106,1],[104,2,106,2],[104,3,106,3],[104,4,106,4],[104,5,106,5],[101,59,102,59],[101,60,102,60],[101,61,102,61],[101,62,102,62],[101,63,102,63],[101,64,102,64],[101,32,102,32],[101,33,102,33],[101,35,102,35],[101,56,102,56],[101,57,102,57],[101,58,102,58],[101,17,102,17],[101,18,102,18],[101,19,102,19],[101,20,102,20],[101,21,102,21],[101,31,102,31],[101,7,102,7],[101,8,102,8],[101,10,102,10],[101,14,102,14],[101,15,102,15],[101,16,102,16],[101,1,102,1],[101,2,102,2],[101,3,102,3],[101,4,102,4],[101,5,102,5],[101,6,102,6],[98,64,99,64],[98,65,99,65],[98,75,99,75],[98,76,99,76],[98,77,99,77],[98,6,99,6],[98,7,99,7],[98,8,99,8],[98,10,99,10],[98,14,99,14],[98,15,99,15],[98,78,99,78],[98,58,99,58],[98,59,99,59],[98,60,99,60],[98,61,99,61],[98,62,99,62],[98,63,99,63],[98,31,99,31],[98,32,99,32],[98,33,99,33],[98,35,99,35],[98,56,99,56],[98,57,99,57],[98,16,99,16],[98,17,99,17],[98,18,99,18],[98,19,99,19],[98,20,99,20],[98,21,99,21],[95,65,96,65],[95,75,96,75],[95,76,96,76],[95,77,96,77],[95,78,96,78],[98,1,99,1],[98,2,99,2],[98,3,99,3],[98,4,99,4],[98,5,99,5],[95,59,96,59],[95,60,96,60],[95,61,96,61],[95,62,96,62],[95,63,96,63],[95,64,96,64],[95,32,96,32],[95,33,96,33],[95,35,96,35],[95,56,96,56],[95,57,96,57],[95,58,96,58],[95,17,96,17],[95,18,96,18],[95,19,96,19],[95,20,96,20],[95,21,96,21],[95,31,96,31],[95,7,96,7],[95,8,96,8],[95,10,96,10],[95,14,96,14],[95,15,96,15],[95,16,96,16],[95,1,96,1],[95,2,96,2],[95,3,96,3],[95,4,96,4],[95,5,96,5],[95,6,96,6],[92,64,93,64],[92,65,93,65],[92,75,93,75],[92,76,93,76],[92,77,93,77],[92,78,93,78],[92,58,93,58],[92,59,93,59],[92,60,93,60],[92,61,93,61],[92,62,93,62],[92,63,93,63],[92,31,93,31],[92,32,93,32],[92,33,93,33],[92,35,93,35],[92,56,93,56],[92,57,93,57],[92,16,93,16],[92,17,93,17],[92,18,93,18],[92,19,93,19],[92,20,93,20],[92,21,93,21],[92,6,93,6],[92,7,93,7],[92,8,93,8],[92,10,93,10],[92,14,93,14],[92,15,93,15],[89,65,90,65],[89,75,90,75],[89,76,90,76],[89,77,90,77],[89,78,90,78],[92,1,93,1],[92,2,93,2],[92,3,93,3],[92,4,93,4],[92,5,93,5],[89,59,90,59],[89,60,90,60],[89,61,90,61],[89,62,90,62],[89,63,90,63],[89,64,90,64],[89,32,90,32],[89,33,90,33],[89,35,90,35],[89,56,90,56],[89,57,90,57],[89,58,90,58],[89,17,90,17],[89,18,90,18],[89,19,90,19],[89,20,90,20],[86,17,87,17],[86,18,87,18],[86,19,87,19],[86,20,87,20],[86,21,87,21],[86,31,87,31],[89,21,90,21],[89,31,90,31],[89,7,90,7],[89,8,90,8],[89,10,90,10],[89,14,90,14],[89,15,90,15],[89,16,90,16],[89,1,90,1],[89,2,90,2],[89,3,90,3],[89,4,90,4],[89,5,90,5],[89,6,90,6],[86,7,87,7],[86,8,87,8],[86,10,87,10],[86,14,87,14],[86,15,87,15],[86,16,87,16],[86,1,87,1],[86,2,87,2],[86,3,87,3],[86,4,87,4],[86,5,87,5],[86,6,87,6],[83,35,84,35],[83,56,84,56],[83,57,84,57],[86,76,87,76],[86,77,87,77],[86,78,87,78],[86,58,87,58],[86,59,87,59],[86,60,87,60],[86,61,87,61],[86,62,87,62],[86,63,87,63],[86,32,87,32],[86,33,87,33],[86,35,87,35],[86,36,87,36],[86,56,87,56],[86,57,87,57],[86,64,87,64],[86,65,87,65],[86,75,87,75],[83,16,84,16],[83,17,84,17],[83,18,84,18],[83,19,84,19],[83,20,84,20],[83,21,84,21],[83,6,84,6],[83,7,84,7],[83,8,84,8],[83,10,84,10],[83,14,84,14],[83,15,84,15],[80,65,81,65],[80,75,81,75],[80,76,81,76],[80,77,81,77],[80,78,81,78],[83,64,84,64],[83,65,84,65],[83,75,84,75],[83,76,84,76],[83,77,84,77],[83,78,84,78],[83,58,84,58],[83,59,84,59],[83,60,84,60],[83,61,84,61],[83,62,84,62],[83,63,84,63],[83,31,84,31],[83,32,84,32],[83,33,84,33],[83,1,84,1],[83,2,84,2],[83,3,84,3],[83,4,84,4],[83,5,84,5],[80,59,81,59],[80,60,81,60],[80,61,81,61],[80,62,81,62],[80,63,81,63],[80,64,81,64],[80,32,81,32],[80,33,81,33],[80,35,81,35],[80,56,81,56],[80,57,81,57],[80,58,81,58],[80,17,81,17],[80,18,81,18],[80,19,81,19],[80,20,81,20],[80,21,81,21],[80,31,81,31],[80,7,81,7],[80,8,81,8],[80,10,81,10],[80,14,81,14],[80,15,81,15],[80,16,81,16],[80,1,81,1],[80,2,81,2],[80,3,81,3],[80,4,81,4],[80,5,81,5],[80,6,81,6],[77,64,78,64],[77,65,78,65],[77,75,78,75],[77,76,78,76],[77,77,78,77],[77,78,78,78],[77,58,78,58],[77,59,78,59],[77,60,78,60],[77,61,78,61],[77,62,78,62],[77,63,78,63],[77,31,78,31],[77,32,78,32],[77,33,78,33],[77,35,78,35],[77,56,78,56],[77,57,78,57],[77,16,78,16],[77,17,78,17],[77,18,78,18],[77,19,78,19],[77,20,78,20],[77,21,78,21],[77,6,78,6],[77,7,78,7],[77,8,78,8],[77,10,78,10],[77,14,78,14],[77,15,78,15],[74,65,75,65],[74,75,75,75],[74,76,75,76],[74,77,75,77],[74,78,75,78],[77,1,78,1],[77,2,78,2],[77,3,78,3],[77,4,78,4],[77,5,78,5],[74,59,75,59],[74,60,75,60],[74,61,75,61],[74,62,75,62],[74,63,75,63],[74,64,75,64],[74,32,75,32],[74,33,75,33],[74,35,75,35],[74,56,75,56],[74,57,75,57],[74,58,75,58],[74,17,75,17],[74,18,75,18],[74,19,75,19],[74,20,75,20],[74,21,75,21],[74,31,75,31],[74,7,75,7],[74,8,75,8],[74,10,75,10],[74,14,75,14],[74,15,75,15],[74,16,75,16],[74,1,75,1],[74,2,75,2],[74,3,75,3],[74,4,75,4],[74,5,75,5],[74,6,75,6],[67,64,72,64],[67,65,72,65],[67,75,72,75],[67,76,72,76],[67,77,72,77],[67,78,72,78],[67,58,72,58],[67,59,72,59],[67,60,72,60],[67,61,72,61],[67,62,72,62],[67,63,72,63],[67,31,72,31],[67,32,72,32],[67,33,72,33],[67,35,72,35],[67,56,72,56],[67,57,72,57],[70,39,72,39],[70,50,72,50],[70,51,72,51],[67,16,72,16],[67,17,72,17],[64,76,65,76],[64,77,65,77],[64,78,65,78],[67,1,72,1],[67,2,72,2],[67,3,72,3],[67,4,72,4],[67,5,72,5],[64,59,65,59],[64,60,65,60],[64,61,65,61],[64,62,65,62],[64,63,65,63],[64,64,65,64],[64,32,65,32],[64,33,65,33],[64,35,65,35],[64,56,65,56],[64,57,65,57],[64,58,65,58],[64,1,65,1],[64,2,65,2],[64,3,65,3],[64,4,65,4],[64,5,65,5],[61,6,62,6],[61,7,62,7],[61,8,62,8],[61,10,62,10],[61,14,62,14],[67,18,72,18],[67,19,72,19],[67,20,72,20],[67,21,72,21],[67,6,72,6],[67,7,72,7],[67,8,72,8],[67,10,72,10],[67,14,72,14],[67,15,72,15],[64,65,65,65],[64,75,65,75],[64,17,65,17],[64,18,65,18],[64,19,65,19],[64,20,65,20],[64,21,65,21],[64,31,65,31],[64,7,65,7],[64,8,65,8],[64,10,65,10],[64,14,65,14],[64,15,65,15],[64,16,65,16],[64,6,65,6],[61,15,62,15],[61,31,62,31],[58,65,59,65],[58,75,59,75],[58,76,59,76],[58,77,59,77],[58,78,59,78],[61,64,62,64],[61,65,62,65],[61,75,62,75],[61,76,62,76],[61,77,62,77],[61,78,62,78],[61,58,62,58],[61,59,62,59],[61,60,62,60],[61,61,62,61],[61,62,62,62],[61,63,62,63],[58,60,59,60],[58,61,59,61],[58,62,59,62],[58,63,59,63],[58,64,59,64],[61,32,62,32],[61,33,62,33],[61,35,62,35],[61,56,62,56],[61,57,62,57],[61,16,62,16],[61,17,62,17],[61,18,62,18],[61,19,62,19],[61,20,62,20],[61,21,62,21],[61,1,62,1],[61,2,62,2],[61,3,62,3],[61,4,62,4],[61,5,62,5],[58,59,59,59],[58,32,59,32],[58,33,59,33],[58,35,59,35],[58,56,59,56],[58,57,59,57],[58,58,59,58],[58,17,59,17],[58,18,59,18],[58,19,59,19],[58,20,59,20],[58,21,59,21],[58,31,59,31],[58,7,59,7],[58,8,59,8],[58,10,59,10],[58,14,59,14],[58,15,59,15],[58,16,59,16],[58,1,59,1],[58,2,59,2],[58,3,59,3],[58,4,59,4],[58,5,59,5],[58,6,59,6],[55,64,56,64],[55,65,56,65],[55,75,56,75],[55,76,56,76],[55,77,56,77],[55,78,56,78],[55,58,56,58],[55,59,56,59],[55,60,56,60],[55,61,56,61],[55,62,56,62],[55,63,56,63],[55,31,56,31],[55,32,56,32],[55,33,56,33],[55,35,56,35],[55,56,56,56],[55,57,56,57],[55,16,56,16],[55,17,56,17],[55,18,56,18],[55,19,56,19],[55,20,56,20],[55,21,56,21],[55,6,56,6],[55,7,56,7],[55,8,56,8],[55,10,56,10],[55,14,56,14],[55,15,56,15],[52,65,53,65],[52,75,53,75],[52,76,53,76],[52,77,53,77],[52,78,53,78],[55,1,56,1],[55,2,56,2],[55,3,56,3],[55,4,56,4],[55,5,56,5],[52,59,53,59],[52,60,53,60],[52,61,53,61],[52,62,53,62],[52,63,53,63],[52,64,53,64],[52,32,53,32],[52,33,53,33],[52,35,53,35],[52,56,53,56],[52,57,53,57],[52,58,53,58],[52,17,53,17],[52,18,53,18],[52,19,53,19],[52,20,53,20],[52,21,53,21],[52,31,53,31],[52,7,53,7],[52,8,53,8],[52,10,53,10],[52,14,53,14],[52,15,53,15],[52,16,53,16],[49,75,50,75],[49,76,50,76],[49,77,50,77],[49,78,50,78],[52,1,53,1],[52,2,53,2],[52,3,53,3],[52,4,53,4],[52,5,53,5],[52,6,53,6],[49,60,50,60],[49,61,50,61],[49,62,50,62],[49,63,50,63],[49,64,50,64],[49,65,50,65],[49,33,50,33],[49,35,50,35],[49,56,50,56],[49,57,50,57],[49,58,50,58],[49,59,50,59],[49,18,50,18],[49,19,50,19],[49,20,50,20],[49,21,50,21],[49,31,50,31],[49,32,50,32],[49,8,50,8],[49,10,50,10],[49,14,50,14],[49,15,50,15],[49,16,50,16],[49,17,50,17],[46,76,47,76],[46,77,47,77],[46,78,47,78],[49,1,50,1],[49,2,50,2],[49,3,50,3],[49,4,50,4],[49,5,50,5],[49,6,50,6],[49,7,50,7],[46,61,47,61],[46,62,47,62],[46,63,47,63],[46,64,47,64],[46,65,47,65],[46,75,47,75],[46,35,47,35],[46,56,47,56],[46,57,47,57],[46,58,47,58],[46,59,47,59],[46,60,47,60],[46,19,47,19],[46,20,47,20],[46,21,47,21],[46,31,47,31],[46,32,47,32],[46,33,47,33],[46,10,47,10],[46,14,47,14],[46,15,47,15],[46,16,47,16],[46,17,47,17],[46,18,47,18],[43,77,44,77],[43,78,44,78],[46,1,47,1],[46,2,47,2],[46,3,47,3],[46,4,47,4],[46,5,47,5],[46,6,47,6],[46,7,47,7],[46,8,47,8],[43,62,44,62],[43,63,44,63],[43,64,44,64],[43,65,44,65],[43,75,44,75],[43,76,44,76],[43,56,44,56],[43,57,44,57],[43,58,44,58],[43,59,44,59],[43,60,44,60],[43,61,44,61],[43,20,44,20],[43,21,44,21],[43,31,44,31],[40,77,41,77],[40,78,41,78],[43,1,44,1],[43,2,44,2],[43,3,44,3],[43,4,44,4],[43,5,44,5],[43,6,44,6],[43,7,44,7],[43,8,44,8],[40,62,41,62],[40,63,41,63],[40,64,41,64],[40,65,41,65],[40,75,41,75],[40,76,41,76],[40,56,41,56],[40,57,41,57],[40,58,41,58],[40,59,41,59],[40,60,41,60],[40,61,41,61],[40,20,41,20],[40,21,41,21],[40,31,41,31],[40,32,41,32],[40,33,41,33],[40,35,41,35],[40,14,41,14],[40,15,41,15],[40,16,41,16],[40,17,41,17],[40,18,41,18],[40,19,41,19],[40,7,41,7],[40,8,41,8],[40,10,41,10],[40,11,44,11],[40,12,44,12],[40,13,44,13],[43,10,44,10],[43,32,44,32],[43,33,44,33],[43,35,44,35],[43,14,44,14],[43,15,44,15],[43,16,44,16],[43,17,44,17],[43,18,44,18],[43,19,44,19],[37,75,38,75],[37,76,38,76],[37,77,38,77],[37,78,38,78],[40,1,41,1],[40,2,41,2],[40,3,41,3],[40,4,41,4],[40,5,41,5],[40,6,41,6],[37,60,38,60],[37,61,38,61],[37,62,38,62],[37,63,38,63],[37,64,38,64],[37,65,38,65],[37,33,38,33],[37,35,38,35],[37,56,38,56],[37,57,38,57],[37,58,38,58],[37,59,38,59],[37,18,38,18],[37,19,38,19],[37,20,38,20],[37,21,38,21],[37,31,38,31],[37,32,38,32],[37,8,38,8],[37,10,38,10],[37,14,38,14],[37,15,38,15],[37,16,38,16],[37,17,38,17],[34,76,35,76],[34,77,35,77],[34,78,35,78],[37,1,38,1],[37,2,38,2],[37,3,38,3],[37,4,38,4],[37,5,38,5],[37,6,38,6],[37,7,38,7],[34,61,35,61],[34,62,35,62],[34,63,35,63],[34,64,35,64],[34,65,35,65],[34,75,35,75],[34,38,35,38],[34,56,35,56],[34,57,35,57],[34,58,35,58],[34,59,35,59],[34,60,35,60],[34,31,35,31],[34,32,35,32],[34,33,35,33],[34,35,35,35],[34,36,35,36],[34,37,35,37],[34,16,35,16],[34,17,35,17],[31,76,32,76],[31,77,32,77],[31,78,32,78],[34,1,35,1],[34,2,35,2],[34,3,35,3],[34,4,35,4],[34,5,35,5],[31,59,32,59]],"merged_total":1216,"flags":["merged_cut"]}
[]
[null,"Room Information",null,null,null,null,null,null,null,null,"Supply",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Transfer Flow",null,null,null,"Exhaust",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Calculated Metrics"]
[null,null,null,null,null,null,null,null,null,null,"System Info",null,null,null,"Qs based on Conditioning",null,"Qs to maintain dP",null,"Qs based on ACH",null,"Room Supply Flows",null,"Box Level  Supply Set Points",null,null,null,"Box Level  Existing                     Supply Set Points",null,"Zone Supply Flows",null,null,null,null,null,null,"System Info",null,null,null,null,"Fume Hood Info",null,null,null,null,null,null,null,null,"Box Flows",null,null,"Duct Transport Velocity ",null,null,null,"Qex based on Conditioning",null,"Qex based on    Exhaust Devices",null,"Qex to maintain dP",null,"Qex based on ACH",null,"Room Exhaust Flows",null,"Box Level Exhaust Set Points",null,null,null,"Zone Exhaust Flows",null,null,null,null,"Resultant ACH"]
[null,null,null,null,null,null,null,null,null,null,"Tags, ID, type, etc.",null,null,null,"Based on heat load","Based on\nsash closed/\nnot in use","Room Exhaust &       Transfer Flow",null,"ACH Exhaust &             Transfer Flow",null,"Max/Min of   Conditioning, dP, & ACH",null,"Based on Current Box Design",null,"Based on Optimized Box Supply Flows",null,"Based on Current BAS Data",null,"Based on Sum of Optimized Box Flows in Zone",null,null,"100 cfm per door","10% of Max Exh.","Greater of per door or 10%",null,"Tags, ID, type, etc.",null,null,null,null,"Dims, Area, etc.",null,null,null,null,null,null,null,null,null,"Sash Open/In Use","Sash Closed/Not In Use","FH Duct","LVRA RCB Criteria","Resultant air velocity","Necessary Flow","Includes Transfer Flow",null,"No GX",null,"Includes GX",null,"@ Occ ACH","@ Unocc ACH","Max/Min based on Exh Devices, dP, Cond., or ACH",null,"Based on Current Box Design",null,"Based on Optimized Exhaust Flows",null,"Based on Sum of Optimized Box Flows in Zone",null,null,null,null,"Based on Room Exhaust Flows"]
[null,"Room #","Room Name","Area\n(ft2)","Height\n(ft)","Volume\n(ft3)","Room Type","Heat Load Label \n(1-5)","Risk Level \n#",null,"AHU\n#","VAV Box\n#","Box   Size","Box Min Flows (cfm)","Max Flow (Full Cooling)\n(cfm)","Min Flow (Full Heating)\n(cfm)","Max Flow based on Max Exhaust\n(cfm)","Min Flow based on Min Exhaust\n(cfm)","Max Flow based on Max ACH Exhaust\n(cfm)","Min Flow based on Min ACH Exhaust\n(cfm)","Room Flow @ Max\n(cfm)","Room Flow @ Min\n(cfm)","Box Supply  Flow @ Max\n(cfm)","Box Supply Flow @ Min\n(cfm)","Supply Box Flow @ Max\n(cfm)","Supply Box Flow @ Min\n(cfm)","Supply Box Flow @ Max\n(cfm)","Supply Box Flow @ Min\n(cfm)","Zone Supply Flow @ Max.\n(cfm)","Zone Supply Flow @ Min.\n(cfm)",null,"Door Transfer Flow\n(cfm)","Flow @ 10%  Max. Device Exh.\n(cfm)","Greater of Door and 10% Max Exh\n(cfm)",null,"Exh. Fan\n#","VVE Box\n#","Box        Size","Min Box Flows (cfm)","Exhaust\nType","RCB Rating ","Retrofit? (y/n)","Total Width (in)","Device Height (in)","Face Width (in)","Hood Depth (in)","Opening Height (in)","Hood Interior Volume (ft3)","Face Area (ft2)","Min ACH based on RCB rating ","Max Flow    (FH @ 18 in.)\n(cfm)","Min Flow (Based on RCB rating & size)\n(cfm)","Duct Diameter (in)","Necessary Duct Velocity (fpm)","Calc. Duct Velocity from Min flow\n(fpm)","Flow of Min Necessary Duct Velocity \n(cfm)","Room Max Flow\n(Full Cooling)\n(cfm)","Room Min Flow\n(Full Heating)\n(cfm)","Room Max Flow\n(ECDs @ Max)\n(cfm)","Room Min Flow\n(ECDs @ Min)\n(cfm)","Room Max Flow \n(cfm)","Room    Min Flow\n(cfm)","Room Max Flow\n(cfm)","Room   Min Flow\n(cfm)","Room   Max Flow\n(cfm)","Room   Min Flow\n(cfm)","Box Exhaust Flow @ Max\n(cfm)","Box Exhaust Flow @ Min\n(cfm)","Box Flow @ Max. Room Exhaust\n(cfm)","Box Flow @ Min. Room Exhaust\n(cfm)","Zone Exhaust Flow @ Max\n(cfm)","Zone Exhaust Flow @ Min\n(cfm)",null,null,null,"Max ACH","Min ACH","Max\ncfm/sf","Min\ncfm/sf",null,"Notes"]
[]
["Example","3111","Tissue Culture",324,9,{"$f":"D7*E7","v":2916},"Lab",1,1,null,"AH-1,   AH-3","M49",110,50,301.058823529412,90.317647058823496,972,972,-2.7999999999999972,-51.4,972,972,null,null,null,null,null,null,null,null,null,-100,100,100,null,"EAH-1, EAH-3","M71",110,50,"BSC",null,null,null,null,"",null,null,"","","",268,268,null,"","","",401.05882352941177,190.31764705882352,1072,1072,1072,1072,97.2,48.6,{"$f":"SUM(AY7:AY12)","v":1072},{"$f":"SUM(AZ7:AZ12)","v":1072},null,null,null,null,null,null,2,2,null,22,22,3.308641975308642,3.308641975308642]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"M72",110,50,"BSC",null,null,null,null,null,null,null,null,null,null,268,268]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,"","BSC",null,null,null,null,null,null,null,null,null,null,268,268]
[]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,"","BSC",null,null,null,null,null,null,null,null,null,null,268,268]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"M5",110,50,"GX",null,null,null,null,null,null,null,null,null,null,0,0]
["x"]
[null,"3115","Chem Lab",1051,9,9459,"Lab",1,0,null,"AH-1,   AH-3","M55",12,240,976.5827886710241,292.97483660130723,0,0,-100,-100,976.5827886710241,292.97483660130723,null,null,null,null,null,null,null,null,null,100,0,100,null,"EAH-1, EAH-3","M52",110,50,"Traditional Fume Hood",0,"n",48,48,39,28,18,30.333333333333332,4.875,0,0,0,10,0,0,0,1076.5827886710199,392.97483660130723,0,0,100,100,0,0,1076.5827886710199,392.97483660130723,null,null,null,null,null,null,1,1,null,6.82894252249302,2.4927043235097193,1.0243413783739523,0.37390564852645786]
[null,null,null,null,null,0,null,null,null,null,null,"M58",12,240,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
["x"]
[null,"3118","Wet  Lab",191,9,1719,"Lab",1,2,null,"AH-1,   AH-3","M69",108,35,177.47603485838781,53.242810457516342,195,195,14.599999999999994,-42.7,195,195,null,null,null,null,null,null,null,null,null,100,25,100,null,"EAH-1, EAH-3","M70",110,50,"Traditional Fume Hood",2,"n",48,48,39,28,18,30.333333333333332,4.875,150,295,295,10,250,540.88811077510741,136.34982638888891,277.47603485838783,153.24281045751633,295,295,295,295,114.6,57.3,295,295,null,null,null,null,null,null,2,2,null,10.296684118673648,10.296684118673648,1.544502617801047,1.544502617801047]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,"Wet Process Station",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,"Wet Process Station",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,"Wet Process Station",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3133","Chem Lab",983,9,8847,"Lab",1,3,null,"AH-1,   AH-3","M3",12,240,913.39760348583877,274.0192810457516,195,195,489.79999999999995,194.89999999999998,913.39760348583877,274.0192810457516,null,null,null,null,null,null,null,null,null,100,25,100,null,"EAH-1, EAH-3","M1",110,50,"Traditional Fume Hood",3,"n",48,48,39,28,18,30.333333333333332,4.875,250,295,295,10,300,540.88811077510741,163.61979166666669,1013.3976034858388,374.0192810457516,295,295,295,295,589.79999999999995,294.89999999999998,1013.3976034858388,374.0192810457516,null,null,null,null,null,null,1,1,null,6.872821997191175,2.5365837982078778,1.0309232995786763,0.3804875697311817]
[null,null,null,null,null,0,null,null,null,null,null,"M4",110,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,"","Traditional Fume Hood",3,"n",48,48,39,28,18,30.333333333333332,4.875,250,295,295,10,300,540.88811077510741,163.61979166666669]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"M2",10,165,"GX",null,null,null,null,null,null,null,null,null,null,718.39760348583877,79.019281045751598,null,"","",""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3137","Bio Lab",479,9,4311,"Lab",1,2,null,"AH-1,   AH-3","M7",112,90,445.08387799564269,133.5251633986928,0,0,187.39999999999998,43.699999999999989,445.08387799564269,133.5251633986928,null,null,null,null,null,null,null,null,null,100,0,100,null,"EAH-1, EAH-3","M6",12,240,"GX",null,null,null,null,"",null,null,"","","",545.08387799564275,233.5251633986928,null,"","","",545.08387799564275,233.5251633986928,0,0,100,100,287.39999999999998,143.69999999999999,545.08387799564275,233.5251633986928,null,null,null,null,null,null,1,1,null,7.586414446703448,3.2501762477201503,1.1379621670055173,0.48752643715802252]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3145","Bio Lab",479,9,4311,"Lab",1,1,null,"AH-1,   AH-3","M26",114,200,445.08387799564269,133.5251633986928,0,0,43.699999999999989,-28.150000000000006,445.08387799564269,133.5251633986928,null,null,null,null,null,null,null,null,null,100,0,100,null,"EAH-1, EAH-3","M24",16,420,"Gx",null,null,null,null,"",null,null,"","","",545.08387799564275,233.5251633986928,null,"","","",545.08387799564275,233.5251633986928,0,0,100,100,143.69999999999999,71.849999999999994,545.08387799564275,233.5251633986928,null,null,null,null,null,null,1,1,null,7.586414446703448,3.2501762477201503,1.1379621670055173,0.48752643715802252]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3147","Bio Lab",498,9,4482,"Lab",1,1,null,"AH-1,   AH-3","M20",112,90,462.73856209150324,138.82156862745097,0,0,49.400000000000006,-25.299999999999997,462.73856209150324,138.82156862745097,null,null,null,null,null,null,null,null,null,100,0,100,null,"EAH-1, EAH-3","M22",110,50,"Traditional Fume Hood",0,"n",48,48,39,28,18,30.333333333333332,4.875,0,0,0,10,0,0,0,562.73856209150324,238.82156862745097,0,0,100,100,149.4,74.7,562.73856209150324,238.82156862745097,null,null,null,null,null,null,1,1,null,7.5333140842236048,3.1970758852403072,1.1299971126335406,0.47956138278604615]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"M19",112,90,"GX",null,null,null,null,null,null,null,null,null,null,562.73856209150324,238.82156862745097,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3150","Autoclave Room",469,9,4221,"Lab",1,1,null,"AH-1,   AH-3","M44",114,200,435.79193899782132,130.73758169934638,50,50,40.699999999999989,-29.650000000000006,435.79193899782132,130.73758169934638,null,null,null,null,null,null,null,null,null,100,25,100,null,"EAH-1, EAH-3","M23",24,795,"Canopy",null,null,null,null,"",null,null,"","","",150,150,null,"","","",535.79193899782126,230.73758169934638,150,150,150,150,140.69999999999999,70.349999999999994,535.79193899782126,230.73758169934638,null,null,null,null,null,null,1,1,null,7.616090106578838,3.2798519075955421,1.1424135159868256,0.4919777861393313]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GX",null,null,null,null,null,null,null,null,null,null,385.79193899782126,80.737581699346379,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3150A","Bio Lab",469,9,4221,"Lab",1,1,null,"AH-1,   AH-3","-",null,"",435.79193899782132,130.73758169934638,436,436,40.699999999999989,-29.650000000000006,436,436,null,null,null,null,null,null,null,null,null,100,50,100,null,"EAH-1, EAH-3","-",null,"","BSC",null,null,null,null,"",null,null,"","","",268,268,null,"","","",535.79193899782126,230.73758169934638,536,536,536,536,140.69999999999999,70.349999999999994,536,536,null,null,null,null,null,null,2,2,null,7.6190476190476186,7.6190476190476186,1.1428571428571428,1.1428571428571428]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"BSC",null,null,null,null,null,null,null,null,null,null,268,268,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3153","Equipment Room",238,9,2142,"Lab",1,0,null,"AH-1,   AH-3","M43",110,50,221.14814814814815,66.344444444444449,0,0,-100,-100,221.14814814814815,66.344444444444449,null,null,null,null,null,null,null,null,null,100,0,100,null,"EAH-1, EAH-3","M28",12,240,"Gx",null,null,null,null,"",null,null,"","","",321.14814814814815,166.34444444444443,null,"","","",321.14814814814815,166.34444444444443,0,0,100,100,0,0,321.14814814814815,166.34444444444443,null,null,null,null,null,null,1,1,null,8.9957464467268391,4.6595082477435419,1.3493619670090258,0.69892623716153124]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3155","Chem Storage",238,9,2142,"Lab",1,2,null,"AH-1,   AH-3",null,null,null,221.14814814814815,66.344444444444449,0,0,42.800000000000011,-28.599999999999994,221.14814814814815,66.344444444444449,null,null,null,null,null,null,null,null,null,100,0,100,null,"EAH-1, EAH-3","n/a",null,"","GX",null,null,null,null,"",null,null,"","","",321.14814814814815,166.34444444444443,null,"","","",321.14814814814815,166.34444444444443,0,0,100,100,142.80000000000001,71.400000000000006,321.14814814814815,166.34444444444443,null,null,null,null,null,null,1,1,null,8.9957464467268391,4.6595082477435419,1.3493619670090258,0.69892623716153124]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3179","General Storage",66,9,594,"Lab",1,0,null,"AH-1,   AH-3","n/a",null,"",61.326797385620921,18.398039215686275,0,0,-100,-100,61.326797385620921,18.398039215686275,null,null,null,null,null,null,null,null,null,100,0,100,null,"EAH-1, EAH-3","P2",110,50,"GX",null,null,null,null,"",null,null,"","","",161.32679738562092,118.39803921568628,null,"","","",161.32679738562092,118.39803921568628,0,0,100,100,0,0,161.32679738562092,118.39803921568628,null,null,null,null,null,null,1,1,null,16.295636099557669,11.959397900574372,2.4443454149336503,1.7939096850861558]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3217","Electrical",66,9,594,"Lab",1,0,null,"AH-1,   AH-3","n/a",null,"",61.326797385620921,18.398039215686275,0,0,0,0,61.326797385620921,18.398039215686275,null,null,null,null,null,null,null,null,null,0,0,0,null,"EAH-1, EAH-3","n/a",null,"","n/a",null,null,null,null,"",null,null,"","","","-","-",null,"","","",61.326797385620921,18.398039215686275,0,0,0,0,0,0,61.326797385620921,18.398039215686275,null,null,null,null,null,null,1,1,null,6.1946259985475676,1.8583877995642704,0.92919389978213518,0.27875816993464053]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3222","Genetics Lab",328,9,2952,"Lab",1,1,null,"AH-4,    AH-6","P8",112,90,304.77559912854031,91.432679738562086,50,0,-1.5999999999999943,-50.8,304.77559912854031,91.432679738562086,null,null,null,null,null,null,null,null,null,100,0,100,null,"EAH-4, EAH-6",111,108,35,"Snorkel",null,null,null,null,"",null,null,"","","",50,50,null,"","","",404.77559912854031,191.43267973856209,50,50,150,100,98.4,49.2,404.77559912854031,191.43267973856209,null,null,null,null,null,null,1,1,null,8.2271463237508193,3.8909081247675221,1.2340719485626228,0.58363621871512827]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P70",16,420,"GX",null,null,null,null,null,null,null,null,null,null,354.77559912854031,141.43267973856209,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3222A","Research Lab",384,9,3456,"Lab",1,1,null,"AH-4,    AH-6","P10",110,50,356.81045751633985,107.04313725490195,195,195,15.200000000000003,-42.4,356.81045751633985,195,null,null,null,null,null,null,null,null,null,100,25,100,null,"EAH-4, EAH-6","P6",110,50,"Traditional Fume Hood",3,"n",48,48,39,28,18,30.333333333333332,4.875,250,295,295,10,300,540.88811077510741,163.61979166666669,456.81045751633985,207.04313725490195,295,295,295,295,115.2,57.6,456.81045751633985,295,null,null,null,null,null,null,1,2,null,7.9307371096586783,5.1215277777777777,1.1896105664488017,0.76822916666666663]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P69",110,50,"GX",null,null,null,null,null,null,null,null,null,null,161.81045751633985,0,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3222B","Chem Lab",384,9,3456,"Lab",1,1,null,"AH-4,    AH-6","P67",108,35,356.81045751633985,107.04313725490195,195,195,15.200000000000003,-42.4,356.81045751633985,195,null,null,null,null,null,null,null,null,null,100,25,100,null,"EAH-4, EAH-6",108,110,50,"Traditional Fume Hood",3,"n",48,48,39,28,18,30.333333333333332,4.875,250,295,295,10,300,540.88811077510741,163.61979166666669,456.81045751633985,207.04313725490195,295,295,295,295,115.2,57.6,456.81045751633985,295,null,null,null,null,null,null,1,2,null,7.9307371096586783,5.1215277777777777,1.1896105664488017,0.76822916666666663]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P69",110,50,"GX",null,null,null,null,null,null,null,null,null,null,161.81045751633985,0,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3222C","Chem Lab",177,9,1593,"Lab",1,1,null,"AH-4,    AH-6","P93",110,50,164.46732026143792,49.340196078431376,195,195,-46.9,-73.45,195,195,null,null,null,null,null,null,null,null,null,100,25,100,null,"EAH-4, EAH-6",109,110,50,"Traditional Fume Hood",3,"n",48,48,39,28,18,30.333333333333332,4.875,250,295,295,10,300,540.88811077510741,163.61979166666669,264.46732026143792,149.34019607843138,295,295,295,295,53.1,26.55,295,295,null,null,null,null,null,null,2,2,null,11.111111111111111,11.111111111111111,1.6666666666666667,1.6666666666666667]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,"no gx",null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3222D","Chem Lab",308,9,2772,"Lab",1,3,null,"AH-4,    AH-6","P4",110,50,286.19172113289761,85.857516339869278,490,490,84.800000000000011,-7.5999999999999943,490,490,null,null,null,null,null,null,null,null,null,100,50,100,null,"EAH-4, EAH-6",110,110,50,"Traditional Fume Hood",3,"n",48,48,39,28,18,30.333333333333332,4.875,250,295,295,10,300,540.88811077510741,163.61979166666669,386.19172113289761,185.85751633986928,590,590,590,590,184.8,92.4,590,590,null,null,null,null,null,null,2,2,null,12.770562770562771,12.770562770562771,1.9155844155844155,1.9155844155844155]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P91",110,50,"Traditional Fume Hood",3,"n",48,48,39,28,18,30.333333333333332,4.875,250,295,295,10,300,540.88811077510741,163.61979166666669]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3225","Large Lab",1495,9,13455,"Lab",1,2,null,"AH-4,    AH-6","P11",112,90,1389.144880174292,416.74346405228761,345,345,697,248.5,1389.144880174292,416.74346405228761,null,null,null,null,null,null,null,null,null,200,50,200,null,"EAH-4, EAH-6","P18",110,50,"Traditional Fume Hood",3,"n",48,48,39,28,18,30.333333333333332,4.875,250,295,295,10,300,540.88811077510741,163.61979166666669,1589.144880174292,616.74346405228766,545,545,545,545,897,448.5,1589.144880174292,616.74346405228766,null,null,null,null,null,null,1,1,null,7.0864877599745464,2.7502495609912492,1.0629731639961819,0.41253743414868738]
[null,null,null,null,null,0,null,null,null,null,null,"P15",112,90,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,103,110,50,"Slot Hood",null,null,null,null,null,null,null,null,null,null,200,200,null,null,null,""]
[null,null,null,null,null,0,null,null,null,null,null,"P21",24,795,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P90",108,35,"Snorkel",null,null,null,null,null,null,null,null,null,null,50,50,null,null,null,""]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,"",0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P7",12,240,"GX",null,null,null,null,null,null,null,null,null,null,1044.144880174292,71.743464052287663,null,null,null,""]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,"",0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P9",112,90,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,"",0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P13",112,90,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3225B","Bioprocess Lab",250,9,2250,"Lab",1,4,null,"AH-4,    AH-6","P3",110,50,232.29847494553377,69.689542483660134,168,168,-25,-62.5,232.29847494553377,168,null,null,null,null,null,null,null,null,null,100,25,100,null,"EAH-4, EAH-6","P1",110,50,"BSC",null,null,null,null,"",null,null,"","","",268,268,null,"","","",332.29847494553377,169.68954248366015,268,268,268,268,75,37.5,{"$f":"10*2250/60","v":375},268,null,null,null,null,null,null,1,2,null,10,7.1466666666666665,1.3291938997821351,1.0720000000000001]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P2",110,50,"BSC",null,null,null,null,null,null,null,null,null,null,268,268,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3225C","Lab",229,9,2061,"Lab",1,0,null,"AH-4,    AH-6","P5",110,50,212.78540305010893,63.835620915032678,0,0,-100,-100,212.78540305010893,63.835620915032678,null,null,null,null,null,null,null,null,null,100,0,100,null,"EAH-4, EAH-6","P7",12,240,"GX",null,null,null,null,"",null,null,"","","",312.78540305010893,163.83562091503268,null,"","","",312.78540305010893,163.83562091503268,0,0,100,100,0,0,312.78540305010893,163.83562091503268,null,null,null,null,null,null,1,1,null,9.1058341499303896,4.7695959509470942,1.3658751224895587,0.71543939264206413]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3225D","Lab",250,9,2250,"Lab",1,1,null,"AH-4,    AH-6","P22",112,90,232.29847494553377,69.689542483660134,0,0,-25,-62.5,232.29847494553377,69.689542483660134,null,null,null,null,null,null,null,null,null,100,0,100,null,"EAH-4, EAH-6","P25",16,420,"GX",null,null,null,null,"",null,null,"","","",332.29847494553377,169.68954248366015,null,"","","",332.29847494553377,169.68954248366015,0,0,100,100,75,37.5,332.29847494553377,169.68954248366015,null,null,null,null,null,null,1,1,null,8.8612926652142345,4.5250544662309373,1.3291938997821351,0.67875816993464055]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3226","Lab",326,9,2934,"Lab",1,0,null,"AH-4,    AH-6","P14",108,35,302.91721132897601,90.875163398692806,0,0,-100,-100,302.91721132897601,90.875163398692806,null,null,null,null,null,null,null,null,null,100,0,100,null,"EAH-4, EAH-6","n/a",null,"","GX",null,null,null,null,"",null,null,"","","",402.91721132897601,190.87516339869279,null,"","","",402.91721132897601,190.87516339869279,0,0,100,100,0,0,402.91721132897601,190.87516339869279,null,null,null,null,null,null,1,1,null,8.2396157735986915,3.9033775746153947,1.2359423660398037,0.58550663619230914]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3228","Autoclave Room",490,9,4410,"Lab",1,0,null,"AH-4,    AH-6","P16",108,35,455.30501089324616,136.59150326797385,50,0,-200,-200,455.30501089324616,136.59150326797385,null,null,null,null,null,null,null,null,null,200,0,200,null,"EAH-4, EAH-6","P19",16,420,"Canopy",null,null,null,null,"",null,null,"","","",50,50,null,"","","",655.30501089324616,336.59150326797385,50,50,250,200,0,0,655.30501089324616,336.59150326797385,null,null,null,null,null,null,1,1,null,8.9157144339217176,4.5794762349384195,1.3373571650882574,0.68692143524076299]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GX",null,null,null,null,null,null,null,null,null,null,605.30501089324616,286.59150326797385,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3228B","Shared Lab",490,9,4410,"Lab",1,0,null,"AH-4,    AH-6","P59",110,50,455.30501089324616,136.59150326797385,0,0,-100,-100,455.30501089324616,136.59150326797385,null,null,null,null,null,null,null,null,null,100,0,100,null,"EAH-4, EAH-6","P54",24,795,"GX",null,null,null,null,"",null,null,"","","",555.30501089324616,236.59150326797385,null,"","","",555.30501089324616,236.59150326797385,0,0,100,100,0,0,555.30501089324616,236.59150326797385,null,null,null,null,null,null,1,1,null,7.5551702162346421,3.2189320172513445,1.1332755324351962,0.48283980258770171]
[null,null,null,null,null,0,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3230","General Lab Space",118,9,1062,"Lab",1,0,null,"AH-4,    AH-6","P30","-",{"$error":"#N/A"},109.64488017429194,32.893464052287584,0,0,-100,-100,109.64488017429194,32.893464052287584,null,null,null,null,null,null,null,null,null,100,0,100,null,"EAH-4, EAH-6","P52",20,535,"GX",null,null,null,null,"",null,null,"","","",209.64488017429193,132.89346405228758,null,"","","",209.64488017429193,132.89346405228758,0,0,100,100,0,0,209.64488017429193,132.89346405228758,null,null,null,null,null,null,1,1,null,11.844343512671861,7.5081053136885645,1.776651526900779,1.1262157970532847]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3240","Shared",79,9,711,"Lab",1,0,null,"AH-4,    AH-6","P23",108,35,73.406318082788673,22.0218954248366,0,0,-100,-100,73.406318082788673,22.0218954248366,null,null,null,null,null,null,null,null,null,100,0,100,null,"EAH-4, EAH-6","P28",6,70,"GX",null,null,null,null,"",null,null,"","","",173.40631808278869,122.0218954248366,null,"","","",173.40631808278869,122.0218954248366,0,0,100,100,0,0,173.40631808278869,122.0218954248366,null,null,null,null,null,null,1,1,null,14.633444563948412,10.297206364965113,2.1950166845922618,1.5445809547447671]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3244","Bio Lab",115,9,1035,"Lab",1,1,null,"AH-4,    AH-6","P33",108,35,106.85729847494552,32.057189542483655,168,168,-65.5,-82.75,168,168,null,null,null,null,null,null,null,null,null,100,25,100,null,"EAH-4, EAH-6","M31",110,50,"BSC",null,null,null,null,"",null,null,"","","",268,268,null,"","","",206.85729847494554,132.05718954248366,268,268,268,268,34.5,17.25,268,268,null,null,null,null,null,null,2,2,null,15.536231884057971,15.536231884057971,2.3304347826086955,2.3304347826086955]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P49",110,50,"GX",null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3247","Shared Lab",354,9,3186,"Lab",1,0,null,"AH-4,    AH-6","107",112,90,328.93464052287584,98.680392156862752,0,0,-100,-100,328.93464052287584,98.680392156862752,null,null,null,null,null,null,null,null,null,100,0,100,null,"EAH-4, EAH-6","P38",16,420,"GX",null,null,null,null,"",null,null,"","","",428.93464052287584,198.68039215686275,null,"","","",428.93464052287584,198.68039215686275,0,0,100,100,0,0,428.93464052287584,198.68039215686275,null,null,null,null,null,null,1,1,null,8.0778651699223314,3.7416269709390351,1.2116797754883499,0.56124404564085528]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,"",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3251","Teaching Lab",1465,9,13185,"Lab",1,2,null,"AH-4,    AH-6","P40",112,90,1361.2690631808277,408.38071895424832,95,95,679,239.5,1361.2690631808277,408.38071895424832,null,null,null,null,null,null,null,null,null,200,25,200,null,"EAH-4, EAH-6","P42",110,50,"Traditional Fume Hood ",3,"n",48,48,39,28,18,30.333333333333332,4.875,250,295,295,10,300,540.88811077510741,163.61979166666669,1561.2690631808277,608.38071895424832,295,295,295,295,879,439.5,1561.2690631808277,608.38071895424832,null,null,null,null,null,null,1,1,null,7.1047511407546198,2.7685129417713235,1.065712671113193,0.41527694126569853]
[null,null,null,null,null,0,null,null,null,null,null,"P43",112,90,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P41",112,90,"GX",null,null,null,null,null,null,null,null,null,null,1266.2690631808277,313.38071895424832,null,null,null,""]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P44",110,50,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3271","Chem Lab",742,9,6678,"Lab",1,2,null,"AH-4,    AH-6","P63",112,90,689.46187363834429,206.83856209150329,190,190,245.2,22.599999999999994,689.46187363834429,206.83856209150329,null,null,null,null,null,null,null,null,null,200,50,200,null,"EAH-4, EAH-6","P57",110,50,"Traditional Fume Hood ",4,"n",48,48,39,28,18,30.333333333333332,4.875,375,390,390,10,500,715.07241763488776,272.69965277777783,889.46187363834429,406.83856209150326,390,390,390,390,445.2,222.6,889.46187363834429,406.83856209150326,null,null,null,null,null,null,1,1,null,7.9915711917191761,3.6553329927358784,1.1987356787578765,0.54829994891038181]
[null,null,null,null,null,0,null,null,null,null,null,"P99",108,35,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P62",112,90,"GX",null,null,null,null,null,null,null,null,null,null,499.46187363834429,16.838562091503263,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3272","Bio process Lab",176,9,1584,"Lab",1,1,null,"AH-4,    AH-6","P64",108,35,163.53812636165577,49.061437908496728,168,168,-47.2,-73.599999999999994,168,168,null,null,null,null,null,null,null,null,null,100,25,100,null,"EAH-4, EAH-6","P65",110,50,"BSC",null,null,null,null,"",null,null,"","","",268,268,null,"","","",263.53812636165577,149.06143790849671,268,268,268,268,52.8,26.4,268,268,null,null,null,null,null,null,2,2,null,10.151515151515152,10.151515151515152,1.5227272727272727,1.5227272727272727]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P68",110,50,"BSC",null,null,null,null,null,null,null,null,null,null,268,268,null,null,null,""]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P100",110,50,"Lam Flow Hood",null,null,null,null,null,null,null,null,null,null,200,200,null,null,null,""]
["x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,"3293","Lab",872,9,7848,"Lab",1,1,null,"AH-4,    AH-6","P66",114,200,810.25708061002183,243.07712418300653,50,0,161.60000000000002,30.800000000000011,810.25708061002183,243.07712418300653,null,null,null,null,null,null,null,null,null,100,0,100,null,"EAH-4, EAH-6","P97",108,35,"Snorkel",null,null,null,null,"",null,null,"","","",50,50,null,"","","",910.25708061002183,343.0771241830065,50,50,150,100,261.60000000000002,130.80000000000001,910.25708061002183,343.0771241830065,null,null,null,null,null,null,1,1,null,6.9591519924313596,2.622913793448062,1.0438727988647039,0.39343706901720932]
[null,null,null,null,null,0,null,null,null,null,null,"P74",114,200,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P72",16,420,"GX",null,null,null,null,null,null,null,null,null,null,860.25708061002183,293.0771241830065,null,null,null,""]
[null,null,null,null,null,0,null,null,null,null,null,"-",null,"",0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P76",24,795,null,null,null,null,null,"",null,null,"","","",null,null,null,"","","",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",""]
["x"]

{"sheet":"ASHRAE Design Levels","index":4,"n_rows":26,"n_cols":1,"rows_kept":26,"cut":false,"hidden":false,"merged":[[25,0,25,8],[9,0,9,7],[10,0,10,7],[14,1,14,8],[15,1,15,8],[16,1,16,8],[17,1,17,8],[18,0,18,8],[20,0,20,8],[21,0,21,8],[23,0,23,8],[24,0,24,8],[8,0,8,8],[0,0,0,8],[1,0,1,8],[4,0,4,8],[6,0,6,8],[7,0,7,8]]}
[" Air Change Recommendations"]
["This Air Change Rate Calculator references air changes recommended by the ASHRAE Classification of Laboratory Ventilation Design Levels based on the risk level (risk control band)."]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["These tables are directly from the ASHRAE Classification of Laboratory Ventilation Design Levels. Refer also to ASHRAE Standard 62.1 for further recommendations."]

{"sheet":"Glossary of Terms","index":5,"n_rows":23,"n_cols":2,"rows_kept":23,"cut":false,"hidden":false,"merged":[[1,0,1,18],[0,0,0,18],[2,1,2,18],[4,1,4,18],[6,1,6,18],[8,1,8,18],[10,1,10,18],[12,1,12,18],[15,1,15,18],[16,1,16,18],[22,1,22,18],[17,1,17,18],[18,1,18,18],[19,1,19,18],[20,1,20,18],[21,1,21,18]]}
["Glossary of Terms"]
["The worksheets in this calculator contain acronyms and terms that may be unfamiliar, and are included in the glossary below as a reference. "]
["ACH ","Air changes per an hour"]
[]
["CFM ","Cubic feet per minute (ft3/min) "]
[]
["Heat Load Label "]
[]
["Risk Control Band","Also referred to as a Risk Level, this quantifies the risk associated with hazards present in the lab space based on a variety of factors, including hazard type, generation method and rate, etc. See LVRA User Guide for more."]
[]
["AHU #","Air handling unit index number. This is defined by your insitution's approach to labeling equipment. "]
[]
["VAV Box # ","Variable Air Volume Box number. This is defined by your insitution's approach to labeling equipment. "]
[]
[]
["Exhaust Type"]
["BSC ","Biological Safety Cabinet"]
["GX ","General Exhaust "]
["Traditional Fume Hood","A traditional fume hood is used to contain ventilation hazards and hosts an enclosed workspace that contains the hazards and removes them via a vent."]
["Wet Process Station","A fume hood with all equiment for wet-process or chemical processing procedures, usually hosts a sink within the enclosed fume hood space. "]
["Box Flow:      Max Flow       (FH @ 18 in.)","Maximum flow is measured with fume hood sash opened to a height of 18 inches. "]
["Canopy","A specific type of fume hood designed to vent non-toxic vapors (e.g. steam, heat,  odors) and does not have an enclosed work area in traditional fume hoods "]
["FPM","Feet per minute. Common imperial unit of measurement for face velocity of fumehoods."]

{"sheet":"Worksheet with Additional Info","index":6,"n_rows":54,"n_cols":76,"rows_kept":54,"cut":false,"hidden":false,"merged":[[48,71,53,71],[48,72,53,72],[48,73,53,73],[48,74,53,74],[41,71,46,71],[41,72,46,72],[41,73,46,73],[41,74,46,74],[48,0,53,0],[48,1,53,1],[48,2,53,2],[48,3,53,3],[48,4,53,4],[48,5,53,5],[48,6,53,6],[48,7,53,7],[48,8,53,8],[48,9,53,9],[48,13,53,13],[48,14,53,14],[48,15,53,15],[48,16,53,16],[48,17,53,17],[48,18,53,18],[34,71,39,71],[34,55,39,55],[34,56,39,56],[34,57,39,57],[34,58,39,58],[41,19,46,19],[41,20,46,20],[41,29,46,29],[41,30,46,30],[41,31,46,31],[41,32,46,32],[41,53,46,53],[41,54,46,54],[41,55,46,55],[41,56,46,56],[41,57,46,57],[34,54,39,54],[48,19,53,19],[48,20,53,20],[48,29,53,29],[48,30,53,30],[34,59,39,59],[34,60,39,60],[34,61,39,61],[34,62,39,62],[34,29,39,29],[34,72,39,72],[34,73,39,73],[34,74,39,74],[41,0,46,0],[41,1,46,1],[41,2,46,2],[41,3,46,3],[41,4,46,4],[41,5,46,5],[41,6,46,6],[41,7,46,7],[41,8,46,8],[41,9,46,9],[41,13,46,13],[41,14,46,14],[41,15,46,15],[41,16,46,16],[41,17,46,17],[41,18,46,18],[34,30,39,30],[34,31,39,31],[34,32,39,32],[34,53,39,53],[34,9,39,9],[34,13,39,13],[34,14,39,14],[34,15,39,15],[34,16,39,16],[34,17,39,17],[34,18,39,18],[34,19,39,19],[34,20,39,20],[34,0,39,0],[34,1,39,1],[34,2,39,2],[34,3,39,3],[34,4,39,4],[34,5,39,5],[34,6,39,6],[34,7,39,7],[34,8,39,8],[27,9,32,9],[27,13,32,13],[27,14,32,14],[27,15,32,15],[27,16,32,16],[27,17,32,17],[27,18,32,18],[27,19,32,19],[27,20,32,20],[27,0,32,0],[27,1,32,1],[27,2,32,2],[27,3,32,3],[27,4,32,4],[27,5,32,5],[27,6,32,6],[27,7,32,7],[27,8,32,8],[13,60,18,60],[13,61,18,61],[13,62,18,62],[13,71,18,71],[13,72,18,72],[13,73,18,73],[13,74,18,74],[20,0,25,0],[20,1,25,1],[20,2,25,2],[20,3,25,3],[20,4,25,4],[20,5,25,5],[20,6,25,6],[20,7,25,7],[20,8,25,8],[20,9,25,9],[20,13,25,13],[20,14,25,14],[20,15,25,15],[20,16,25,16],[20,17,25,17],[20,18,25,18],[20,19,25,19],[1,1,1,8],[2,71,2,74],[13,0,18,0],[13,1,18,1],[13,2,18,2],[13,3,18,3],[13,4,18,4],[13,5,18,5],[13,6,18,6],[13,7,18,7],[13,8,18,8],[13,9,18,9],[13,13,18,13],[13,14,18,14],[13,15,18,15],[13,16,18,16],[13,17,18,17],[13,18,18,18],[13,19,18,19],[13,20,18,20],[13,29,18,29],[1,9,1,28],[1,29,2,31],[1,71,1,74],[2,9,2,12],[2,13,2,14],[2,15,2,16],[2,17,2,18],[2,19,2,20],[1,32,1,68],[2,63,2,66],[2,67,2,68],[3,9,3,12],[3,15,3,16],[3,17,3,18],[3,19,3,20],[3,21,3,22],[3,23,3,24],[2,49,2,52],[2,53,2,54],[2,55,2,56],[2,57,2,58],[2,59,2,60],[2,61,2,62],[2,21,2,24],[2,25,2,26],[2,27,2,28],[2,32,2,36],[2,37,2,45],[2,46,2,48],[3,57,3,58],[3,61,3,62],[3,63,3,64],[3,65,3,66],[3,67,3,68],[3,71,3,74],[3,25,3,26],[3,27,3,28],[3,32,3,36],[3,37,3,45],[3,53,3,54],[3,55,3,56],[6,7,11,7],[6,8,11,8],[6,9,11,9],[6,13,11,13],[6,14,11,14],[6,15,11,15],[6,1,11,1],[6,2,11,2],[6,3,11,3],[6,4,11,4],[6,5,11,5],[6,6,11,6],[6,30,11,30],[6,31,11,31],[6,32,11,32],[6,53,11,53],[6,54,11,54],[6,55,11,55],[6,16,11,16],[6,17,11,17],[6,18,11,18],[6,19,11,19],[6,20,11,20],[6,29,11,29],[6,62,11,62],[6,71,11,71],[6,72,11,72],[6,73,11,73],[6,74,11,74],[6,56,11,56],[6,57,11,57],[6,58,11,58],[6,59,11,59],[6,60,11,60],[6,61,11,61],[13,30,18,30],[13,31,18,31],[13,32,18,32],[13,53,18,53],[13,54,18,54],[13,55,18,55],[13,56,18,56],[13,57,18,57],[13,58,18,58],[20,30,25,30],[20,31,25,31],[20,32,25,32],[20,53,25,53],[20,54,25,54],[20,55,25,55],[20,56,25,56],[20,57,25,57],[20,58,25,58],[20,74,25,74],[27,32,32,32],[27,53,32,53],[27,54,32,54],[27,55,32,55],[27,56,32,56],[27,57,32,57],[27,58,32,58],[27,59,32,59],[27,60,32,60],[27,61,32,61],[20,60,25,60],[20,61,25,61],[20,62,25,62],[20,71,25,71],[20,72,25,72],[20,73,25,73],[20,59,25,59],[27,62,32,62],[27,71,32,71],[27,72,32,72],[27,73,32,73],[27,74,32,74],[6,0,11,0],[41,58,46,58],[41,59,46,59],[41,60,46,60],[41,61,46,61],[41,62,46,62],[48,31,53,31],[48,32,53,32],[48,53,53,53],[48,54,53,54],[48,55,53,55],[48,56,53,56],[48,57,53,57],[48,58,53,58],[48,59,53,59],[48,60,53,60],[48,61,53,61],[48,62,53,62],[27,29,32,29],[27,30,32,30],[27,31,32,31],[13,59,18,59],[20,20,25,20],[20,29,25,29]]}
[]
[null,"Room Information",null,null,null,null,null,null,null,"Supply",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Transfer Flow",null,null,"Exhaust",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Calculated Metrics"]
[null,null,null,null,null,null,null,null,null,"System Info",null,null,null,"Qs based on Conditioning",null,"Qs to maintain dP",null,"Qs based on ACH",null,"Room Supply Flows",null,"Box Level  Supply Set Points",null,null,null,"Box Level  Existing                     Supply Set Points",null,"Zone Supply Flows",null,null,null,null,"System Info",null,null,null,null,"Fume Hood Info",null,null,null,null,null,null,null,null,"Box Flows",null,null,"Duct Transport Velocity ",null,null,null,"Qex bas on Conditioning",null,"Qex based on Exhaust Devices",null,"Qex to maintain dP",null,"Qex based on ACH",null,"Room Exhaust Flows",null,"Box Level Exhaust Set Points",null,null,null,"Zone Exhaust Flows",null,null,null,"Air Change Rates"]
[null,null,null,null,null,null,null,null,null,"Tags, ID, type, etc.",null,null,null,"Based on heat load","Based on\nsash closed/\nnot in use","Room Exhaust &       Transfer Flow",null,"ACH Exhaust & Transfer Flow",null,"Max/Min of   Conditioning, dP, & ACH",null,"Based on Current Box Design",null,"Based on Optimized Box Supply Flows",null,"Based on Current BAS Data",null,"Based on Sum of Optimized Box Flows in Zone",null,"100 cfm per door","10% of Max Exh.","Greater of per door or 10%","Tags, ID, type, etc.",null,null,null,null,"Dims, Area, etc.",null,null,null,null,null,null,null,null,null,"Sash Open/In Use","Sash Closed/Not In Use","FH Duct","LVRA RCB Criteria","Resultant air velocity","Necessary Flow","Includes Transfer Flow",null,"No GX",null,"Includes GX",null,"@ Occ ACH","@ Unocc ACH","Max/Min based on Exh Devices, dP, Cond., or ACH",null,"Based on Current Box Design",null,"Based on Optimized Exhaust Flows",null,"Based on Sum of Optimized Box Flows in Zone",null,null,null,"Based on Room Exhaust Flows"]
[null,"Room #","Room Name","Area\n(ft2)","Height\n(ft)","Volume\n(ft3)","Room Type","Heat Load Label \n(1-5)","Risk Level #","AHU #","VAV Box #","Box Size","Box Min Flows (cfm)","Max Flow (Full Cooling)\n(cfm)","Min Flow (Full Heating)\n(cfm)","Max Flow based on Max Exhaust\n(cfm)","Min Flow based on Min Exhaust\n(cfm)","Max Flow based on Max ACH Exhaust\n(cfm)","Min Flow based on Min ACH Exhaust\n(cfm)","Room Flow @ Max\n(cfm)","Room Flow @ Min\n(cfm)","Box Supply  Flow @ Max\n(cfm)","Box Supply Flow @ Min\n(cfm)","Supply Box Flow @ Max\n(cfm)","Supply Box Flow @ Min\n(cfm)","Supply Box Flow @ Max\n(cfm)","Supply Box Flow @ Min\n(cfm)","Zone Supply Flow @ Max.\n(cfm)","Zone Supply Flow @ Min.\n(cfm)","Door Transfer Flow\n(cfm)","Flow @ 10%  Max. Device Exh.\n(cfm)","Greater of Door and 10% Max Exh\n(cfm)","Exh. Fan\n#","VVE Box\n#","Box        Size","Min Box Flows (cfm)","Exhaust\nType","RCB Rating ","Retrofit? (y/n)","Total Width (in)","Device Height (in)","Face Width (in)","Hood Depth (in)","Opening Height (in)","Hood Interior Volume (ft3)","Face Area (ft2)","Min ACH based on RCB rating ","Max Flow (FH @ 18 in.)\n(cfm)","Min Flow (Based on RCB rating & size)\n(cfm)","Duct Diameter (in)","Necessary Duct Velocity (fpm)","Calc. Duct Velocity from Min flow\n(fpm)","Flow of Min Necessary Duct Velocity \n(cfm)","Room Max Flow\n(Full Cooling)\n(cfm)","Room Min Flow\n(Full Heating)\n(cfm)","Room Max Flow\n(ECDs @ Max)\n(cfm)","Room Min Flow\n(ECDs @ Min)\n(cfm)","Room Max Flow \n(cfm)","Room Min Flow\n(cfm)","Room Max Flow\n(cfm)","Room   Min Flow\n(cfm)","Room   Max Flow\n(cfm)","Room   Min Flow\n(cfm)","Box Exhaust Flow @ Max\n(cfm)","Box Exhaust Flow @ Min\n(cfm)","Box Flow @ Max. Room Exhaust\n(cfm)","Box Flow @ Min. Room Exhaust\n(cfm)","Zone Exhaust Flow @ Max\n(cfm)","Zone Exhaust Flow @ Min\n(cfm)",null,null,"Max ACH","Min ACH","Max\ncfm/sf","Min\ncfm/sf","Notes"]
[]
["Example","3111","Tissue Culture",324,9,{"$f":"D7*E7","v":2916},"Lab",1,1,"AH-1,   AH-3","M49",110,50,301.058823529412,90.317647058823496,972,972,-2.7999999999999972,-51.4,972,972,null,null,null,null,null,null,null,null,-100,100,100,"EAH-1, EAH-3","M71",110,50,"BSC",null,null,null,null,"",null,null,"","","",268,268,null,"","","",401.05882352941177,190.31764705882352,1072,1072,1072,1072,97.2,48.6,{"$f":"SUM(AV7:AV12)","v":1072},{"$f":"SUM(AW7:AW12)","v":1072},null,null,null,null,null,null,2,2,{"$f":"(60*'Worksheet with Additional Info'!BJ7)/('Worksheet with Additional Info'!F7)","v":22.057613168724281},{"$f":"(60*BK7)/('Worksheet with Additional Info'!F7)","v":22.057613168724281},3.308641975308642,3.308641975308642]
[null,null,null,null,null,0,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"M72",110,50,"BSC",null,null,null,null,null,null,null,null,null,null,268,268]
[null,null,null,null,null,0,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,"","BSC",null,null,null,null,null,null,null,null,null,null,268,268]
[]
[null,null,null,null,null,0,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-",null,"","BSC",null,null,null,null,null,null,null,null,null,null,268,268]
[null,null,null,null,null,0,null,null,null,null,"-",null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"M5",110,50,"GX",null,null,null,null,null,null,null,null,null,null,0,0]
[]
[null,null,null,null,null,{"$f":"D14*E14","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"(60*'Worksheet with Additional Info'!BJ14)/('Worksheet with Additional Info'!F14)","v":{"$error":"#DIV/0!"}},{"$f":"(60*BK14)/('Worksheet with Additional Info'!F14)","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,0]
[null,null,null,null,null,0]
[]
[null,null,null,null,null,0]
[null,null,null,null,null,0]
[]
[null,null,null,null,null,{"$f":"D21*E21","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"(60*'Worksheet with Additional Info'!BJ21)/('Worksheet with Additional Info'!F21)","v":{"$error":"#DIV/0!"}},{"$f":"(60*BK21)/('Worksheet with Additional Info'!F21)","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,0]
[null,null,null,null,null,0]
[]
[null,null,null,null,null,0]
[null,null,null,null,null,0]
[]
[null,null,null,null,null,{"$f":"D28*E28","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"(60*'Worksheet with Additional Info'!BJ28)/('Worksheet with Additional Info'!F28)","v":{"$error":"#DIV/0!"}},{"$f":"(60*BK28)/('Worksheet with Additional Info'!F28)","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,0]
[null,null,null,null,null,0]
[]
[null,null,null,null,null,0]
[null,null,null,null,null,0]
[]
[null,null,null,null,null,{"$f":"D35*E35","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"(60*'Worksheet with Additional Info'!BJ35)/('Worksheet with Additional Info'!F35)","v":{"$error":"#DIV/0!"}},{"$f":"(60*BK35)/('Worksheet with Additional Info'!F35)","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,0]
[null,null,null,null,null,0]
[]
[null,null,null,null,null,0]
[null,null,null,null,null,0]
[]
[null,null,null,null,null,{"$f":"D42*E42","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"(60*'Worksheet with Additional Info'!BJ42)/('Worksheet with Additional Info'!F42)","v":{"$error":"#DIV/0!"}},{"$f":"(60*BK42)/('Worksheet with Additional Info'!F42)","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,0]
[null,null,null,null,null,0]
[]
[null,null,null,null,null,0]
[null,null,null,null,null,0]
[]
[null,null,null,null,null,{"$f":"D49*E49","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"(60*'Worksheet with Additional Info'!BJ49)/('Worksheet with Additional Info'!F49)","v":{"$error":"#DIV/0!"}},{"$f":"(60*BK49)/('Worksheet with Additional Info'!F49)","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,0]
[null,null,null,null,null,0]
[]
[null,null,null,null,null,0]
[null,null,null,null,null,0]