## Drop down Menu (hidden)
Yes | Low
Partial | Medium
No | High
NA | NA

## Instructions
Smart Labs Checklist Instructions: Building Capabilities • Start with the Building Capabilities sheet • The capabilities sheet is divided into Air, Water, Lighting, Control, and Energy • Read each line and determine if the building has this capability. If it does select “Yes”, if it some of the capabilities select “Partial”, if it doesn’t have any select “No” and if it is not applicable select “NA”. • The “Impact” column shouldn’t need to be adjusted unless your building or campus mission dictates differently. • Add any observations about the capabilities, or deficiencies and any recommended actions. • The score at the bottom will automatically adjust and anything above 90% has been the goal. Building Operations • Start with the Building Operations sheet • The operations sheet is divided into Air, Water, Lighting, Control, and Energy • The first column represents the correlation of the operational functions to the capabilities • Read each line and determine if the building operational meets this requirement. If it does select “Yes”, if it some of the operations select “Partial”, if it doesn’t have any select “No” and if it is not applicable select “NA”. • The “Impact” column shouldn’t need to be adjusted unless your building or campus mission dictates differently. • Add any observations about the operations, or deficiencies and any recommended actions. • The score at the bottom will automatically adjust and anything above 90% has been the goal. Labs • Start with the Lab sheet (copy new lab sheets as needed for each lab) • The lab sheet is divided into each labs capabilities and operations • The first column represents the correlation of the building capabilities • Read each line and determine if the lab capabilities and operations meet this requirement. If it does select “Yes”, if some of them do select “Partial”, if it doesn’t have any select “No” and if it is not applicable select “NA”. • The “Impact” column shouldn’t need to be adjusted unless your lab or lab mission dictates differently. • Add any observations about the operations, or deficiencies and any recommended actions. • The score at the bottom will automatically adjust and anything above 90% has been the goal. Credit: BOCC Energy Group Pacific Northwest National Laboratory ST Belew SS Paulsen TJ Pfaffle J Su-Coker Contact: ST Belew 509-375-7549 shan.belew@pnnl.gov

## Building Capabilities
SmartLabs Building Capabilities
Building Capabilities
| Capability |  | Present | Impact | Observation | Recommended actions
Air
| A1 | HVAC energy recovery (cools & heats) on lab supply | Yes | High |  |  | 10 | 75 | 75 | 750
| A2 | Variable frequency drives on fan motors with static pressure sensors | Yes | High |  |  | 10 | 75 | 75 | 750
| A3 | Variable air volume lab supply & exhaust terminals | Yes | High |  |  | 10 | 75 | 75 | 750
| A4 | HVAC energy recovery (cools & heats) non-lab | Yes | Low |  |  | 10 | 10 | 10 | 100
| A5 | HVAC Zones for temperature control in offices (VAV) | Yes | Medium |  |  | 10 | 30 | 30 | 300
| A6 | Common stack for exhaust system | Yes | Medium |  |  | 10 | 30 | 30 | 300
| A7 | Exhaust stack heights designed for optimal plume height* | Yes | Low |  |  | 10 | 10 | 10 | 100
| A8 | Office and lab ventilation systems appropriately separated (e.g. Once through air is limited in the office) | Yes | High |  |  | 10 | 75 | 75 | 750
| A9 | Appropriate vestibules and doors for adjacent zones | Yes | Medium |  |  | 10 | 30 | 30 | 300
| A10 | High efficiency motors on ahus, supply, exhaust | Yes | Medium |  |  | 10 | 30 | 30 | 300
| A11 | Fan coil units in mechanical, electrical rooms, data, etc. | Yes | Low |  |  | 10 | 10 | 10 | 100
| A12 | Fan powered boxes/FCUs on perimeter office zones | Yes | Low |  |  | 10 | 10 | 10 | 100
| A13 | Lab/Office/Outside pressure monitoring | Yes | Medium |  |  | 10 | 30 | 30 | 300
| A14 | Supply/exhaust air flow monitors (either stations or phoenix summations) | Yes | Low |  |  | 10 | 10 | 10 | 100
| A15 | DP sensors across lab supply/exhaust VAV (venturis, vav boxes, etc.) | Yes | Low |  |  | 10 | 10 | 10 | 100
| A16 | High Efficiency filters for lab supply air, filters on heat recovery coils in exhaust | Yes | Low |  |  | 10 | 10 | 10 | 100
| A17 | Office HVAC includes economizers | Yes | Low |  |  | 10 | 10 | 10 | 100
| A18 | Lab Supply AHU has DDC control | Yes | High |  |  | 10 | 75 | 75 | 750
| A19 | Lab Supply AHU dehumidification/humidification control | Yes | Low |  |  | 10 | 10 | 10 | 100
| A20 | Office HVAC uses demand control ventilation (CO2) | Yes | Low |  |  | 10 | 10 | 10 | 100
| A21 | For fumehood driven labs, are fumehoods equiped with zone presence sensors | Yes | Low |  |  | 10 | 10 | 10 | 100
| A22 | Snorkels with user controls | Yes | Low
| Water | [5 empty] | FALSE | FALSE | FALSE | 0
| W1 | Variable frequency drives on pump motors with DP sensors at end-of-line | Yes | High |  |  | 10 | 75 | 75 | 750
| W2 | High efficiency condensing boilers | Yes | Medium |  |  | 10 | 30 | 30 | 300
| W3 | High efficiency chillers | Yes | Medium |  |  | 10 | 30 | 30 | 300
| W4 | Zone re-heat/re-cool | Yes | Medium |  |  | 10 | 30 | 30 | 300
| W5 | Water side economizer for chilled water (building, process chilled water) | Yes | Medium |  |  | 10 | 30 | 30 | 300
| W6 | Process chilled water for lab cooling equipment/lab fan coil | Yes | Medium |  |  | 10 | 30 | 30 | 300
| Lighting | [5 empty] | FALSE | FALSE | FALSE | 0
| L1 | Led lighting in all spaces | Yes | High |  |  | 10 | 75 | 75 | 750
| L2 | Lighting system uses occupancy sensors | Yes | High |  |  | 10 | 75 | 75 | 750
| L3 | Lighting control system | Yes | Low |  |  | 10 | 10 | 10 | 100
| L4 | Daylight light level sensors in perimeter offices/labs | Yes | Low |  |  | 10 | 10 | 10 | 100
| Controls | [5 empty] | FALSE | FALSE | FALSE | 0
| C1 | Building automation system for building systems | Yes | High |  |  | 10 | 75 | 75 | 750
| C2 | Temperature sensors in each lab/office zone | Yes | High |  |  | 10 | 75 | 75 | 750
| C3 | BAS information layer/fault detection diagnostics | Yes | Medium |  |  | 10 | 30 | 30 | 300
| C4 | Electronic controls (DDC) | Yes | Medium |  |  | 10 | 30 | 30 | 300
| C5 | Occupancy sensors in labs for HVAC/Lights | Yes | High |  |  | 10 | 75 | 75 | 750
| C6 | Occupancy sensors in offices, support spaces for HVAC/Lights | Yes | Low |  |  | 10 | 10 | 10 | 100
| C7 | Wind velocity sensor for stacks | Yes | Medium |  |  | 10 | 30 | 30 | 300
| C8 | Labs are setup with different modes for airflow (occupied, unoccupied, standby, bypass, vacant) | Yes | Medium |  |  | 10 | 30 | 30 | 300
| Energy | [5 empty] | FALSE | FALSE | FALSE | 0
| E1 | Whole building water meter installed | Yes | Medium |  |  | 10 | 30 | 30 | 300
| E2 | Whole building electrical meter installed | Yes | Medium |  |  | 10 | 30 | 30 | 300
| E3 | Whole building gas meter installed | Yes | Medium |  |  | 10 | 30 | 30 | 300
| E4 | Whole building chilled water meter installed | Yes | Medium |  |  | 10 | 30 | 30 | 300
| E5 | Appropriate meters are in place by system to calculate energy usage (ahus, boilers, chillers, heat recovery) | Yes | Low |  |  | 10 | 10 | 10 | 100
|  |  | 100% |  |  |  |  | 440 | 15150 | 15150
correlates to lab checklist

## Building Operations
SmartLabs Building Operations
Building Operations
| Operations |  | Present | Impact | Observations | Recommendation Action
Air
| A1 | Energy recovery is performing well (both heating & cooling) for labs | Yes | High |  |  | 10 | 75 | 75 | 750
| A2 | Static pressure control is utilized on supply and exhaust fans | Yes | High |  |  | 10 | 75 | 75 | 750
| A3 | VAV minimums and maximums are established for Labs | Yes | High |  |  | 10 | 75 | 75 | 750
| A4 | Energy recovery is performing well for heating & cooling for offices | Yes | Low |  |  | 10 | 10 | 10 | 100
| A5 | VAV minimums and maximums are established for offices | Yes | Medium |  |  | 10 | 30 | 30 | 300
| A6 | Exhaust fans run in parallel, with lead/lag configuration | Yes | Medium |  |  | 10 | 30 | 30 | 300
| A7 | Exhaust fan minimum speeds are maintained to maintain minimum and maximum outlet velocities | Yes | Low |  |  | 10 | 10 | 10 | 100
| A8 | Office HVAC setbacks off hours/weekends, holidays, with optimal starts | Yes | High |  |  | 10 | 75 | 75 | 750
| A9 | Doors between areas and on vestibules are kept closed and monitored if left open | Yes | Low |  |  | 10 | 10 | 10 | 100
| A10 | High efficiency motors are included in specs and replacements | Yes | Medium |  |  | 10 | 30 | 30 | 300
| A11 | Mechanical, electrical rooms, data rooms are maintained at unoccupied temperatures 24/7 | Yes | Low |  |  | 10 | 10 | 10 | 100
| A12 | Perimeter offices zones when hit unoccupied temps start off-hours and don’t start the main AHU | Yes | Low |  |  | 10 | 10 | 10 | 100
| A13 | Lab/Office/Outside pressures are monitored & alarmed | Yes | Medium |  |  | 10 | 30 | 30 | 300
| A14 | Supply and exhaust total CFMs are monitored | Yes | Low |  |  | 10 | 10 | 10 | 100
| A15 | Supply and exhaust fans use static pressure reset | Yes | Low |  |  | 10 | 10 | 10 | 100
| A16 | Filters are monitored and changed based up condition based | Yes | Low |  |  | 10 | 10 | 10 | 100
| A17 | Office HVAC uses economizer operation for free cooling | Yes | Low |  |  | 10 | 10 | 10 | 100
| A18 | Supply air temperature reset is used on AHUs | Yes | Medium |  |  | 10 | 30 | 30 | 300
| A19 | Dehumidification & humidification lockout control used | Yes | Medium |  |  | 10 | 30 | 30 | 300
| A20 | Fresh air is controlled to maintain CO2 levels less than 700 above background | Yes | Low |  |  | 10 | 10 | 10 | 100
| A21 | ability to accommodate snorkel airflows fluctuations | Yes | Low |  |  | 10 | 10 | 10 | 100
| A22 | Corridor and support spaces air exchange rates established at minimum | Yes | Low
| Water | [5 empty] | FALSE | FALSE | FALSE | 0
| W1 | Pumps control to DP and utilize a DP reset for both chilled water and heating hot water | Yes | Low |  |  | 10 | 10 | 10 | 100
| W1 | Heating hot water temperature reset is used | Yes | Medium |  |  | 10 | 30 | 30 | 300
| W2 | Heating return water is maintained below 130, boilers stage upon efficiency curves | Yes | Medium |  |  | 10 | 30 | 30 | 300
| W3 | Chilled water temperature reset is used, and chillers are staged upon efficiency curves | Yes | Low |  |  | 10 | 10 | 10 | 100
| W4 | Labs each have independent heating and cooling setpoints that don’t drive the main AHU DAT temps | Yes | Medium |  |  | 10 | 30 | 30 | 300
| W5 | When outdoor conditions are favorable for a water side economizer (free cooling, cooling tower or AHU configuration) | Yes | Medium |  |  | 10 | 30 | 30 | 300
| W6 | process chilled water is set to a cool temp (50-60F) | Yes | Low |  |  | 10 | 10 | 10 | 100
| Lighting | [5 empty] | FALSE | FALSE | FALSE | 0
| L2/L3 | Lighting zones shutoff when unoccupied | Yes | High |  |  | 10 | 75 | 75 | 750
| L4 | Lights dim in response to daylight in perimeter areas | Yes | Low |  |  | 10 | 10 | 10 | 100
| Controls | [5 empty] | FALSE | FALSE | FALSE | 0
| C1 | Sequence of operations and defined and functionally verified (commissioned) | Yes | High |  |  | 10 | 75 | 75 | 750
| C2 | Appropriate setpoint deadbands are used for lab zones | Yes | Medium |  |  | 10 | 30 | 30 | 300
| C2 | Wide zone setpoint deadbands are used for office zones | Yes | Low |  |  | 10 | 10 | 10 | 100
| C3 | Faults are generated, checked and integral into operations | Yes | Medium |  |  | 10 | 30 | 30 | 300
| C4 | labs setback airflow & temperature when unoccupied | Yes | High |  |  | 10 | 75 | 75 | 750
| C5 | offices setback airflow & temperature when unoccupied based upon a occupancy sensors | Yes | Low |  |  | 10 | 10 | 10 | 100
| C7 | Exhaust stack velocity is controlled per actual wind velocity from sensors | Yes | Medium |  |  | 10 | 30 | 30 | 300
| C8 | Labs are setup with different modes for airflow (occupied, unoccupied, standby, bypass, vacant) | Yes | Medium |  |  | 10 | 30 | 30 | 300
| Energy | [5 empty] | FALSE | FALSE | FALSE | 0
| E1 | Water consumption is benchmarked and tracked | Yes | Medium |  |  | 10 | 30 | 30 | 300
| E2 | Electrical consumption is benchmarked and tracked | Yes | Medium |  |  | 10 | 30 | 30 | 300
| E3 | Gas consumption is benchmarked and tracked | Yes | Medium |  |  | 10 | 30 | 30 | 300
| E2 E3 E4 | Total energy consuption is benchmarked and tracked | Yes | Medium |  |  | 10 | 30 | 30 | 300
| E5 | Energy consumption by system (ahus, boilers, chillers, heat recovery) | Yes | Low |  |  | 10 | 10 | 10 | 100
|  |  | 100% |  |  |  |  | 430 | 12450 | 12450
Note on E34: test: Changed from partial to yes
test:
Changed from partial to yes

## Lab XXXX
SmartLabs - Lab Checklist
3850 GPCL - Lab 112
| Capability |  | Metric | Impact | Notes | Recommended Action
| A3 | Lab supply and exhaust valves are VAV (venturi) | Yes | High |  |  | 10 | 75 | 75 | 750
| C1 | a building automation system is connected | Yes | High |  |  | 10 | 75 | 75 | 750
| C3 | a fault detection and diagnostics system is connected | Yes | Medium |  |  | 10 | 30 | 30 | 300
| L1 | Lab has LED lighting | Yes | Medium |  |  | 10 | 30 | 30 | 300
| C5 | Occupancy sensors for both (lighting & HVAC) | Yes | High |  |  | 10 | 75 | 75 | 750
| A22 | Snorkels have user controls to shutoff (i.e. damper or switch) | Yes | Low |  |  | 10 | 10 | 10 | 100
| A14 | Monitoring lab supply/exhuast, fumehood cfm values | Yes | High |  |  | 10 | 75 | 75 | 750
| W6 | Process chilled water for lab cooling equipment/lab fan coil | NA | Medium |  |  | FALSE | 30 | 0 | 0
| A19 | Lab has individual humidity control | Yes | Low |  |  | 10 | 10 | 10 | 100
| A21 | For fumehood driven labs, are fumehoods equipped with zone presence sensors | NA | Low |  |  | FALSE | 10 | 0 | 0
|  |  | 100% |  |  |  | 80 | 4200 | 3800 | 3800
| Operations |  | Metric | Impact | Notes | Recommended Action
| A3 C5 | Lab airflows setback when lab is unoccupied as detected by occupancy sensors | NA | High |  |  | FALSE | 75 | 0 | 0
| C1 C2 C5 | Lab air temperatures setback when lab is unoccupied as detected by occupancy sensors | Yes | Medium |  |  | 10 | 30 | 30 | 300
| C1 C2 C5 | Lab air temperatures setback when lab is standby mode per schedule | Yes | Medium |  |  | 10 | 30 | 30 | 300
| A19 C5 | humidity is controlled per activity | Yes | Low |  |  | 10 | 10 | 10 | 100
| C1 C2 C5 | Lab has a occupied/unoccupied schedule, including holidays | Yes | Medium |  |  | 10 | 30 | 30 | 300
| C1 | The occupied setpoints for heating and cooling have adequate dead band | Yes | Low |  |  | 10 | 10 | 10 | 100
| C1 | Volumetric offset through BAS | Yes | High |  |  | 10 | 75 | 75 | 750
| C1 | Lab has its own BAS graphic and up-to-date | Yes | Low |  |  | 10 | 10 | 10 | 100
| C1 | Sequence of operation is up-to-date and functional verified | Yes | High |  |  | 10 | 75 | 75 | 750
| C3 | Fault detection is active (no indications of wasted energy or faulty equipment) | Yes | Medium |  |  | 10 | 30 | 30 | 300
| C1 | Minimum ACH driver defined. Includes hoods, cooling, lab type, etc. | Yes | High |  |  | 10 | 75 | 75 | 750
| A3 | Room volume reduce for cabinets, fixed objects | Yes | High |  |  | 10 | 75 | 75 | 750
|  |  | 100% |  |  |  | 110 |  | 4500 | 4500